## Daily report
Daily Operation & Maintenance Report for Kyodo _ Solar project 1.09 MWp
COVER SHEET |  |  | Ref No | 0
|  |  | Revision | 0 | Page No.
PROJECT | KYODO ROOFTOP PHOTOVOLTAIC POWER PROJECT
THE OWNER | KYODO SOJITZ FEED
THE CONTRACTOR | SHARP ENERGY SOLUTION JSC
Document No. | 0
Prepareed by :
Checked by :
Issue date :
|  |  |  | DC capacity : | 1092855 | (kWp)
I. Summary information :
2024-06-10 | Cumulative Energy Yield | Cumulative Irradiance |  | Performance Ratio@STC | Remark
1900-01-01 | (kWh) | ( kWh/m2 ) |  | (°C)
All data | 442 | 0.81345 |  | 49.72%
Data according to EPC contract | 403.1916 | 0.72848 |  | 50.64%
Peak power ( kW) - Actual | 290
CO2 reduction ( ton CO2) | 0.31912 |  |  |  | CO2 reduction factor | 0.722
Money savings | 3885858
II. Graph
III. Event
Công thức tính toán PR :
1. Loại bỏ dữ liệu
- Cần loại bỏ các dữ liệu tính toán nếu : Bức xạ nhỏ hơn 50W/m2
- Loại bỏ các dữ liệu nếu control <100%
2. Quy trình tính toán PR
- Loại bỏ dữ liệu tính toán như mục 1
- Hiệu chỉnh công suất phát về 25*C theo nhiệt độ tấm pin nếu nhiệt độ tấm pin >25*C :
P25deg.C = Pactual ／{ 1 – k x (T(t) – 25) }
Trong đó :
P25deg.C : công suất đã được hiệu chỉnh về 25*C
k : Hệ số suy giảm công suất theo nhiệt độ
T(t) : Nhiệt độ tấm pin theo thời gian
- Tính toán PR theo công thức :
PR = Tổng Sản lượng DMT / Công suất mặc định của hệ thống ĐMT / Tổng Bức xạ

## Raw data
PROJECT | KYODO ROOFTOP PHOTOVOLTAIC POWER PROJECT | [7 empty] | THK-Daily report- 2024-06-10 |  |  |  |  | 3885858
Contractor | SHARP ENERGY SOLUTION JSC | [6 empty] | 0.7221 | 0.722
2024-06-10
|  |  |  | General | [5 empty] | Load consumption | [5 empty] | INVERTER | [63 empty] | INVERTER
|  |  |  | Meter 1- ACC1 panel | [5 empty] | Load |  | Grid |  | Gen |  | INV-01 | [15 empty] | INV-02 | [15 empty] | INV-03 | [15 empty] | INV-04 | [15 empty] | INV-05 | [15 empty] | INV-06
Date/Time | Total Cummulative Energy | Cummulative Energy Today | Total Active Power | Cummulative Energy | Active Power 1 | Irradiance | Irradiance-R1 | PV Temperature | Ambient Temperature | Total load consumption | Active Power | Grid Energy total | Grid Active Power | Grid Energy total | Grid Active Power | Active Power | Total Energy | Today Energy | %Control | Current1 | Current2 | Current3 | Current4 | Current5 | Current6 | Current7 | Current8 | Current9 | Current10 | Current11 | Current12 | Active Power | Total Energy | Today Energy | %Control | Current1 | Current2 | Current3 | Current4 | Current5 | Current6 | Current7 | Current8 | Current9 | Current10 | Current11 | Current12 | Active Power | Total Energy | Today Energy | %Control | Current1 | Current2 | Current3 | Current4 | Current5 | Current6 | Current7 | Current8 | Current9 | Current10 | Current11 | Current12 | Active Power | Total Energy | Today Energy | %Control | Current1 | Current2 | Current3 | Current4 | Current5 | Current6 | Current7 | Current8 | Current9 | Current10 | Current11 | Current12 | Active Power | Total Energy | Today Energy | %Control | Current1 | Current2 | Current3 | Current4 | Current5 | Current6 | Current7 | Current8 | Current9 | Current10 | Current11 | Current12 | Active Power | Total Energy | Today Energy | %Control | Current1 | Current2 | Current3 | Current4 | Current5 | Current6 | Current7 | Current8 | Current9 | Current10 | Current11 | Current12 | Total Output Power (w temp. correct.) | Control
| (kWh) | (kWh) | (kW) | (kWh) | (kW) | (W/m2) | (W/m2) | (C) | (C) | (kWh) | (kW) | (kWh) | (kW) | (kWh) | (kW) | (kW) | (kWh) | (kWh) | % | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (kW) | (kWh) | (kWh) | % | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (kW) | (kWh) | (kWh) | % | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (kW) | (kWh) | (kWh) | % | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (kW) | (kWh) | (kWh) | % | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (kW) | (kWh) | (kWh) | % | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A) | (A)
2025-11-27 | 1179146 | 2707 | 0 | 1179146 | 0 | -2 | -4 | 22.508 | 24.4452 | 4910953 | 345 | 3713407 | 345 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:01 | 1179146 | 2707 | 0 | 1179146 | 0 | -2 | -4 | 22.508 | 24.4452 | 4910959 | 346 | 3713413 | 346 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:02 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.4703 | 24.417 | 4910965 | 361 | 3713419 | 361 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:03 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 22.4609 | 24.3981 | 4910971 | 357 | 3713425 | 357 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:04 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.4421 | 24.3793 | 4910977 | 405 | 3713431 | 405 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:05 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.4139 | 24.3887 | 4910984 | 395 | 3713438 | 395 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:06 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.4045 | 24.3887 | 4910990 | 410 | 3713444 | 410 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:07 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.3763 | 24.3887 | 4910997 | 400 | 3713451 | 400 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:08 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.3669 | 24.3981 | 4911004 | 385 | 3713458 | 385 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:09 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.3481 | 24.3981 | 4911010 | 355 | 3713464 | 355 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:10 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.3481 | 24.3981 | 4911016 | 353 | 3713470 | 353 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:11 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.3105 | 24.3417 | 4911022 | 378 | 3713476 | 378 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:12 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 22.3011 | 24.3511 | 4911028 | 367 | 3713482 | 367 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:13 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.2823 | 24.3511 | 4911034 | 361 | 3713488 | 361 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:14 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.2823 | 24.3323 | 4911040 | 350 | 3713494 | 350 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:15 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.2635 | 24.3229 | 4911046 | 350 | 3713500 | 350 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:16 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.2635 | 24.3229 | 4911052 | 357 | 3713506 | 357 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:17 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.254 | 24.3229 | 4911057 | 362 | 3713511 | 362 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:18 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.254 | 24.2947 | 4911063 | 351 | 3713517 | 351 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:19 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.2352 | 24.2947 | 4911069 | 364 | 3713523 | 364 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:20 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.2258 | 24.2947 | 4911076 | 356 | 3713530 | 356 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:21 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.207 | 24.2571 | 4911081 | 360 | 3713535 | 360 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:22 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 22.1882 | 24.2477 | 4911087 | 358 | 3713541 | 358 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:23 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.1788 | 24.2383 | 4911093 | 346 | 3713547 | 346 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:24 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 22.1694 | 24.163 | 4911099 | 367 | 3713553 | 367 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:25 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.1412 | 24.1442 | 4911105 | 347 | 3713559 | 347 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:26 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 22.1318 | 24.1537 | 4911110 | 343 | 3713564 | 343 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:27 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 22.113 | 24.1066 | 4911116 | 339 | 3713570 | 339 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:28 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.0848 | 24.1348 | 4911122 | 337 | 3713576 | 337 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:29 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.0754 | 24.116 | 4911128 | 343 | 3713582 | 343 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:30 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.066 | 24.1348 | 4911134 | 397 | 3713588 | 397 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:31 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.0472 | 24.0972 | 4911141 | 383 | 3713595 | 383 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:32 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.0472 | 24.1066 | 4911147 | 392 | 3713601 | 392 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:33 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.0378 | 24.1066 | 4911153 | 400 | 3713607 | 400 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:34 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.0284 | 24.0972 | 4911160 | 387 | 3713614 | 387 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:35 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.0189 | 24.0878 | 4911166 | 356 | 3713620 | 356 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:36 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.0189 | 24.0878 | 4911172 | 352 | 3713626 | 352 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:37 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.0189 | 24.0878 | 4911178 | 365 | 3713632 | 365 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:38 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.0189 | 24.0972 | 4911184 | 371 | 3713638 | 371 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:39 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 22.0001 | 24.0408 | 4911191 | 358 | 3713645 | 358 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:40 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.9813 | 24.0408 | 4911196 | 359 | 3713650 | 359 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:41 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.9531 | 24.0596 | 4911202 | 347 | 3713656 | 347 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:42 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.9437 | 24.0502 | 4911208 | 341 | 3713662 | 341 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:43 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.9437 | 24.0032 | 4911214 | 342 | 3713668 | 342 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:44 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.9343 | 23.9562 | 4911220 | 339 | 3713674 | 339 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:45 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.9061 | 23.9938 | 4911225 | 342 | 3713679 | 342 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:46 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.8967 | 23.9938 | 4911231 | 344 | 3713685 | 344 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:47 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.8967 | 23.9656 | 4911237 | 336 | 3713691 | 336 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:48 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.8591 | 23.9656 | 4911242 | 337 | 3713696 | 337 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:49 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.8591 | 23.9468 | 4911248 | 350 | 3713702 | 350 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:50 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.8309 | 23.9279 | 4911254 | 340 | 3713708 | 340 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:51 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.8027 | 23.9186 | 4911260 | 361 | 3713714 | 361 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:52 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.7933 | 23.9279 | 4911265 | 342 | 3713719 | 342 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:53 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.7556 | 23.9091 | 4911271 | 341 | 3713725 | 341 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:54 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.7462 | 23.8621 | 4911277 | 342 | 3713731 | 342 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:55 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.718 | 23.8621 | 4911283 | 403 | 3713737 | 403 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:56 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.718 | 23.8527 | 4911290 | 384 | 3713744 | 384 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:57 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.7086 | 23.8621 | 4911296 | 414 | 3713750 | 414 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:58 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.6898 | 23.8527 | 4911303 | 413 | 3713757 | 413 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 00:59 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.671 | 23.8527 | 4911310 | 407 | 3713764 | 407 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:00 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.6428 | 23.8339 | 4911317 | 381 | 3713771 | 381 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:01 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.6146 | 23.8057 | 4911323 | 377 | 3713777 | 377 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:02 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.5958 | 23.7869 | 4911330 | 371 | 3713784 | 371 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:03 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.5582 | 23.7775 | 4911336 | 365 | 3713790 | 365 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:04 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.5299 | 23.7681 | 4911342 | 375 | 3713796 | 375 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:05 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.5205 | 23.7681 | 4911348 | 363 | 3713802 | 363 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:06 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.5111 | 23.7399 | 4911354 | 343 | 3713808 | 343 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:07 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.4829 | 23.7211 | 4911360 | 338 | 3713814 | 338 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:08 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.4829 | 23.6835 | 4911365 | 335 | 3713819 | 335 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:09 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.4735 | 23.6835 | 4911371 | 335 | 3713825 | 335 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:10 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.4829 | 23.6458 | 4911377 | 338 | 3713831 | 338 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:11 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.4735 | 23.6646 | 4911382 | 338 | 3713836 | 338 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:12 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.4735 | 23.6646 | 4911387 | 338 | 3713841 | 338 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:13 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.4735 | 23.6176 | 4911394 | 344 | 3713848 | 344 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:14 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.4829 | 23.5894 | 4911399 | 338 | 3713853 | 338 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:15 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.4829 | 23.6176 | 4911405 | 404 | 3713859 | 404 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:16 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.5017 | 23.627 | 4911412 | 407 | 3713866 | 407 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:17 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.5111 | 23.6364 | 4911419 | 403 | 3713873 | 403 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:18 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.5299 | 23.58 | 4911425 | 357 | 3713879 | 357 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:19 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.5488 | 23.5988 | 4911431 | 357 | 3713885 | 357 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:20 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.5299 | 23.5988 | 4911438 | 402 | 3713892 | 402 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:21 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.5299 | 23.6176 | 4911444 | 384 | 3713898 | 384 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:22 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.5299 | 23.5518 | 4911451 | 383 | 3713905 | 383 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:23 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.5205 | 23.5706 | 4911457 | 379 | 3713911 | 379 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:24 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.5205 | 23.58 | 4911464 | 379 | 3713918 | 379 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:25 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.5205 | 23.5894 | 4911470 | 349 | 3713924 | 349 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:26 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.5205 | 23.5706 | 4911475 | 349 | 3713929 | 349 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:27 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.5111 | 23.5706 | 4911481 | 352 | 3713935 | 352 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:28 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.5111 | 23.5518 | 4911487 | 352 | 3713941 | 352 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:29 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.5017 | 23.5424 | 4911493 | 345 | 3713947 | 345 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:30 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.5017 | 23.5424 | 4911499 | 337 | 3713953 | 337 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:31 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.4829 | 23.5236 | 4911505 | 340 | 3713959 | 340 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:32 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.4829 | 23.5048 | 4911510 | 339 | 3713964 | 339 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:33 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.4735 | 23.5048 | 4911516 | 336 | 3713970 | 336 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:34 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.4735 | 23.5048 | 4911521 | 342 | 3713975 | 342 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:35 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.4641 | 23.5424 | 4911527 | 334 | 3713981 | 334 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:36 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.4641 | 23.5048 | 4911533 | 335 | 3713987 | 335 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:37 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.4641 | 23.5048 | 4911538 | 340 | 3713992 | 340 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:38 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.4547 | 23.5048 | 4911544 | 334 | 3713998 | 334 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:39 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.4547 | 23.4954 | 4911549 | 325 | 3714003 | 325 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:40 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.4171 | 23.486 | 4911555 | 327 | 3714009 | 327 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:41 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.3889 | 23.486 | 4911560 | 324 | 3714014 | 324 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:42 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.3889 | 23.4766 | 4911566 | 322 | 3714020 | 322 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:43 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.3701 | 23.486 | 4911571 | 323 | 3714025 | 323 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:44 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.3607 | 23.4766 | 4911576 | 326 | 3714030 | 326 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:45 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.3607 | 23.4295 | 4911582 | 329 | 3714036 | 329 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:46 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.3607 | 23.4107 | 4911588 | 386 | 3714042 | 386 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:47 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.3419 | 23.4013 | 4911594 | 373 | 3714048 | 373 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:48 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.3231 | 23.3825 | 4911600 | 373 | 3714054 | 373 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:49 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.3137 | 23.3637 | 4911606 | 374 | 3714060 | 374 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:50 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.2854 | 23.3637 | 4911613 | 376 | 3714067 | 376 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:51 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.2478 | 23.3355 | 4911619 | 344 | 3714073 | 344 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:52 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.229 | 23.2979 | 4911625 | 342 | 3714079 | 342 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:53 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.2196 | 23.2227 | 4911630 | 339 | 3714084 | 339 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:54 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.182 | 23.2227 | 4911636 | 341 | 3714090 | 341 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:55 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.1444 | 23.2603 | 4911642 | 358 | 3714096 | 358 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:56 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.135 | 23.2697 | 4911647 | 331 | 3714101 | 331 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:57 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.0974 | 23.2132 | 4911653 | 326 | 3714107 | 326 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:58 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.0597 | 23.2227 | 4911658 | 326 | 3714112 | 326 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 01:59 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 21.0504 | 23.1944 | 4911664 | 326 | 3714118 | 326 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:00 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.0315 | 23.1756 | 4911669 | 324 | 3714123 | 324 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:01 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 21.0033 | 23.1192 | 4911675 | 324 | 3714129 | 324 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:02 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.9657 | 23.1474 | 4911680 | 328 | 3714134 | 328 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:03 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.9563 | 23.1474 | 4911686 | 329 | 3714140 | 329 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:04 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.9469 | 23.1286 | 4911691 | 329 | 3714145 | 329 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:05 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.9469 | 23.1286 | 4911696 | 330 | 3714150 | 330 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:06 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.9375 | 23.1286 | 4911702 | 327 | 3714156 | 327 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:07 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.9093 | 23.1192 | 4911708 | 324 | 3714162 | 324 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:08 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.9093 | 23.1192 | 4911713 | 345 | 3714167 | 345 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:09 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.8999 | 23.0722 | 4911719 | 345 | 3714173 | 345 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:10 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.8999 | 23.1004 | 4911725 | 346 | 3714179 | 346 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:11 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.8905 | 23.0628 | 4911730 | 344 | 3714184 | 344 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:12 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.8717 | 23.0252 | 4911736 | 331 | 3714190 | 331 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:13 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.8623 | 23.0346 | 4911741 | 331 | 3714195 | 331 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:14 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.8435 | 23.0252 | 4911747 | 330 | 3714201 | 330 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:15 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.8153 | 23.0252 | 4911752 | 326 | 3714206 | 326 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:16 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.8153 | 23.0346 | 4911758 | 327 | 3714212 | 327 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:17 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.7964 | 23.0252 | 4911763 | 319 | 3714217 | 319 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:18 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.7776 | 23.0346 | 4911769 | 321 | 3714223 | 321 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:19 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.7682 | 23.0064 | 4911774 | 333 | 3714228 | 333 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:20 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.7212 | 22.9876 | 4911780 | 372 | 3714234 | 372 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:21 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.7024 | 22.9781 | 4911786 | 367 | 3714240 | 367 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:22 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.6742 | 22.9405 | 4911792 | 370 | 3714246 | 370 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:23 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.6554 | 22.9405 | 4911799 | 386 | 3714253 | 386 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:24 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.6366 | 22.9311 | 4911805 | 338 | 3714259 | 338 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:25 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.6178 | 22.9123 | 4911810 | 338 | 3714264 | 338 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:26 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.5896 | 22.8747 | 4911816 | 336 | 3714270 | 336 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:27 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.5707 | 22.8841 | 4911822 | 335 | 3714276 | 335 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:28 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.5613 | 22.8841 | 4911827 | 335 | 3714281 | 335 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:29 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.5425 | 22.9123 | 4911833 | 324 | 3714287 | 324 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:30 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.5425 | 22.8653 | 4911838 | 324 | 3714292 | 324 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:31 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.5331 | 22.8277 | 4911844 | 328 | 3714298 | 328 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:32 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4955 | 22.8277 | 4911849 | 329 | 3714303 | 329 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:33 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4861 | 22.8371 | 4911855 | 324 | 3714309 | 324 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:34 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4767 | 22.8183 | 4911860 | 328 | 3714314 | 328 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:35 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4673 | 22.7995 | 4911865 | 323 | 3714319 | 323 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:36 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4673 | 22.7807 | 4911871 | 327 | 3714325 | 327 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:37 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4673 | 22.7713 | 4911876 | 327 | 3714330 | 327 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:38 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4485 | 22.7807 | 4911882 | 327 | 3714336 | 327 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:39 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4391 | 22.7901 | 4911887 | 334 | 3714341 | 334 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:40 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4297 | 22.7995 | 4911893 | 338 | 3714347 | 338 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:41 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4297 | 22.7901 | 4911898 | 331 | 3714352 | 331 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:42 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4297 | 22.7525 | 4911904 | 327 | 3714358 | 327 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:43 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4203 | 22.7525 | 4911909 | 329 | 3714363 | 329 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:44 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4203 | 22.7525 | 4911915 | 343 | 3714369 | 343 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:45 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4203 | 22.7525 | 4911921 | 385 | 3714375 | 385 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:46 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4203 | 22.7525 | 4911927 | 367 | 3714381 | 367 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:47 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4203 | 22.7525 | 4911934 | 363 | 3714388 | 363 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:48 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4297 | 22.7431 | 4911940 | 377 | 3714394 | 377 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:49 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4203 | 22.7337 | 4911946 | 363 | 3714400 | 363 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:50 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4015 | 22.7054 | 4911951 | 329 | 3714405 | 329 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:51 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.3921 | 22.7243 | 4911957 | 324 | 3714411 | 324 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:52 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4015 | 22.7243 | 4911962 | 325 | 3714416 | 325 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:53 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4015 | 22.7243 | 4911968 | 327 | 3714422 | 327 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:54 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4203 | 22.6866 | 4911973 | 306 | 3714427 | 306 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:55 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4015 | 22.7243 | 4911978 | 305 | 3714432 | 305 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:56 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.4015 | 22.6866 | 4911983 | 312 | 3714437 | 312 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:57 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.3827 | 22.602 | 4911988 | 311 | 3714442 | 311 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:58 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.3827 | 22.6114 | 4911994 | 309 | 3714448 | 309 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 02:59 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.3545 | 22.6396 | 4911999 | 313 | 3714453 | 313 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:00 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.3451 | 22.6114 | 4912004 | 254 | 3714458 | 254 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:01 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.3451 | 22.5926 | 4912008 | 255 | 3714462 | 255 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:02 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.3262 | 22.5926 | 4912012 | 249 | 3714466 | 249 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:03 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.3074 | 22.5832 | 4912016 | 256 | 3714470 | 256 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:04 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.2886 | 22.5644 | 4912020 | 237 | 3714474 | 237 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:05 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.3074 | 22.5644 | 4912024 | 229 | 3714478 | 229 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:06 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.2886 | 22.555 | 4912028 | 236 | 3714482 | 236 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:07 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.2792 | 22.5362 | 4912032 | 233 | 3714486 | 233 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:08 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.2792 | 22.4891 | 4912036 | 234 | 3714490 | 234 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:09 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.251 | 22.4986 | 4912040 | 294 | 3714494 | 294 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:10 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.2416 | 22.508 | 4912045 | 283 | 3714499 | 283 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:11 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 20.204 | 22.4609 | 4912050 | 278 | 3714504 | 278 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:12 | 1179146 | 0 | 0 | 1179146 | 0 | -3 | -6 | 20.1664 | 22.4233 | 4912054 | 281 | 3714508 | 281 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:13 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.1476 | 22.4609 | 4912059 | 275 | 3714513 | 275 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:14 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.1194 | 22.4891 | 4912064 | 254 | 3714518 | 254 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:15 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.1005 | 22.4421 | 4912068 | 252 | 3714522 | 252 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:16 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.0629 | 22.4609 | 4912072 | 250 | 3714526 | 250 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:17 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.0535 | 22.3763 | 4912076 | 245 | 3714530 | 245 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:18 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.0253 | 22.3951 | 4912080 | 250 | 3714534 | 250 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:19 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.0159 | 22.4139 | 4912084 | 234 | 3714538 | 234 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:20 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 20.0065 | 22.3575 | 4912088 | 232 | 3714542 | 232 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:21 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9971 | 22.3669 | 4912092 | 234 | 3714546 | 234 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:22 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9783 | 22.3575 | 4912096 | 231 | 3714550 | 231 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:23 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9689 | 22.3293 | 4912100 | 231 | 3714554 | 231 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:24 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9689 | 22.3293 | 4912104 | 260 | 3714558 | 260 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:25 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9501 | 22.3481 | 4912109 | 307 | 3714563 | 307 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:26 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9501 | 22.2823 | 4912114 | 299 | 3714568 | 299 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:27 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9313 | 22.3105 | 4912119 | 251 | 3714573 | 251 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:28 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9313 | 22.2823 | 4912123 | 271 | 3714577 | 271 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:29 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9313 | 22.3199 | 4912127 | 235 | 3714581 | 235 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:30 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9313 | 22.3105 | 4912131 | 236 | 3714585 | 236 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:31 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9313 | 22.3199 | 4912135 | 235 | 3714589 | 235 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:32 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9313 | 22.3293 | 4912139 | 238 | 3714593 | 238 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:33 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9313 | 22.3105 | 4912143 | 290 | 3714597 | 290 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:34 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9501 | 22.2823 | 4912148 | 275 | 3714602 | 275 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:35 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9501 | 22.2823 | 4912153 | 284 | 3714607 | 284 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:36 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9313 | 22.3011 | 4912157 | 305 | 3714611 | 305 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:37 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9501 | 22.3105 | 4912163 | 300 | 3714617 | 300 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:38 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9501 | 22.3011 | 4912168 | 300 | 3714622 | 300 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:39 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9313 | 22.2823 | 4912172 | 265 | 3714626 | 265 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:40 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9125 | 22.2729 | 4912177 | 262 | 3714631 | 262 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:41 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9031 | 22.2635 | 4912181 | 261 | 3714635 | 261 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:42 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.9031 | 22.2823 | 4912185 | 261 | 3714639 | 261 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:43 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.8843 | 22.2823 | 4912190 | 265 | 3714644 | 265 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:44 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.8749 | 22.3011 | 4912194 | 249 | 3714648 | 249 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:45 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.8654 | 22.3105 | 4912198 | 231 | 3714652 | 231 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:46 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.8654 | 22.2823 | 4912202 | 229 | 3714656 | 229 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:47 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.8654 | 22.2258 | 4912206 | 228 | 3714660 | 228 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:48 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.8654 | 22.207 | 4912209 | 229 | 3714663 | 229 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:49 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.8372 | 22.254 | 4912213 | 227 | 3714667 | 227 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:50 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.8278 | 22.2164 | 4912217 | 231 | 3714671 | 231 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:51 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.809 | 22.2352 | 4912221 | 235 | 3714675 | 235 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:52 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.7808 | 22.2164 | 4912225 | 239 | 3714679 | 239 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:53 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.7714 | 22.2164 | 4912229 | 232 | 3714683 | 232 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:54 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.7714 | 22.2164 | 4912233 | 234 | 3714687 | 234 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:55 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.7714 | 22.2164 | 4912237 | 232 | 3714691 | 232 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:56 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.7714 | 22.2164 | 4912240 | 228 | 3714694 | 228 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:57 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.7808 | 22.2164 | 4912244 | 227 | 3714698 | 227 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:58 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.7714 | 22.16 | 4912249 | 293 | 3714703 | 293 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 03:59 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.762 | 22.1318 | 4912253 | 275 | 3714707 | 275 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:00 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.762 | 22.0942 | 4912256 | 145 | 3714710 | 145 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:01 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.7432 | 22.0472 | 4912259 | 138 | 3714713 | 138 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:02 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.7432 | 22.066 | 4912261 | 135 | 3714715 | 135 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:03 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.762 | 22.113 | 4912263 | 107 | 3714717 | 107 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:04 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.7432 | 22.1224 | 4912265 | 169 | 3714719 | 169 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:05 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.7432 | 22.0848 | 4912268 | 172 | 3714722 | 172 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:06 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.7432 | 22.0754 | 4912270 | 172 | 3714724 | 172 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:07 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.7432 | 22.0754 | 4912273 | 174 | 3714727 | 174 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:08 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.7338 | 22.0848 | 4912276 | 164 | 3714730 | 164 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:09 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.7244 | 22.0754 | 4912279 | 162 | 3714733 | 162 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:10 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.7244 | 22.0848 | 4912282 | 168 | 3714736 | 168 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:11 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.715 | 22.0848 | 4912284 | 164 | 3714738 | 164 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:12 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.715 | 22.0754 | 4912287 | 169 | 3714741 | 169 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:13 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.6868 | 22.0378 | 4912290 | 163 | 3714744 | 163 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:14 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.6774 | 22.066 | 4912293 | 168 | 3714747 | 168 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:15 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.668 | 22.0378 | 4912296 | 175 | 3714750 | 175 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:16 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.6492 | 22.0378 | 4912298 | 171 | 3714752 | 171 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:17 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.6492 | 22.0378 | 4912301 | 166 | 3714755 | 166 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:18 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.6398 | 22.0378 | 4912304 | 180 | 3714758 | 180 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:19 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.6398 | 22.066 | 4912307 | 184 | 3714761 | 184 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:20 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.621 | 22.0472 | 4912309 | 113 | 3714763 | 113 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:21 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.6398 | 22.0378 | 4912311 | 111 | 3714765 | 111 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:22 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.621 | 22.0378 | 4912313 | 156 | 3714767 | 156 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:23 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.6398 | 22.0189 | 4912316 | 140 | 3714770 | 140 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:24 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.6398 | 22.0001 | 4912318 | 145 | 3714772 | 145 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:25 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.6398 | 22.0189 | 4912321 | 156 | 3714775 | 156 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:26 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.6398 | 21.9907 | 4912323 | 162 | 3714777 | 162 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:27 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.621 | 22.0001 | 4912326 | 173 | 3714780 | 173 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:28 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.621 | 22.0284 | 4912328 | 117 | 3714782 | 117 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:29 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.621 | 21.9813 | 4912330 | 114 | 3714784 | 114 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:30 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.6398 | 21.9813 | 4912332 | 109 | 3714786 | 109 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:31 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.6492 | 21.9343 | 4912333 | 107 | 3714787 | 107 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:32 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.6398 | 21.9813 | 4912335 | 96 | 3714789 | 96 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:33 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.6492 | 21.9719 | 4912337 | 95 | 3714791 | 95 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:34 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.6398 | 21.9531 | 4912338 | 95 | 3714792 | 95 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:35 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.6398 | 21.9531 | 4912340 | 118 | 3714794 | 118 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:36 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.621 | 21.9719 | 4912342 | 97 | 3714796 | 97 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:37 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.621 | 21.9719 | 4912343 | 94 | 3714797 | 94 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:38 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.621 | 21.9531 | 4912345 | 95 | 3714799 | 95 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:39 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.6021 | 21.9343 | 4912346 | 96 | 3714800 | 96 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:40 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.5927 | 21.9719 | 4912348 | 96 | 3714802 | 96 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:41 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.5833 | 21.9531 | 4912350 | 95 | 3714804 | 95 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:42 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.5551 | 21.9249 | 4912351 | 103 | 3714805 | 103 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:43 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.5457 | 21.9061 | 4912353 | 101 | 3714807 | 101 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:44 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.5457 | 21.9061 | 4912355 | 110 | 3714809 | 110 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:45 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.5457 | 21.9249 | 4912356 | 96 | 3714810 | 96 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:46 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.5457 | 21.9061 | 4912358 | 93 | 3714812 | 93 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:47 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.5269 | 21.8873 | 4912360 | 154 | 3714814 | 154 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:48 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.5269 | 21.8873 | 4912362 | 138 | 3714816 | 138 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:49 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4987 | 21.8497 | 4912365 | 137 | 3714819 | 137 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:50 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4893 | 21.8497 | 4912367 | 142 | 3714821 | 142 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:51 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4893 | 21.8497 | 4912369 | 139 | 3714823 | 139 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:52 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4799 | 21.8497 | 4912372 | 111 | 3714826 | 111 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:53 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4799 | 21.8121 | 4912373 | 109 | 3714827 | 109 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:54 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4799 | 21.8403 | 4912375 | 107 | 3714829 | 107 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:55 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4799 | 21.8497 | 4912377 | 109 | 3714831 | 109 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:56 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4611 | 21.8309 | 4912379 | 100 | 3714833 | 100 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:57 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4517 | 21.8403 | 4912381 | 104 | 3714835 | 104 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:58 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4517 | 21.8121 | 4912383 | 107 | 3714837 | 107 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 04:59 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4423 | 21.8121 | 4912384 | 104 | 3714838 | 104 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:00 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4423 | 21.8309 | 4912386 | 103 | 3714840 | 103 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:01 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4423 | 21.8027 | 4912388 | 103 | 3714842 | 103 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:02 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4423 | 21.8309 | 4912390 | 109 | 3714844 | 109 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:03 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4423 | 21.8121 | 4912392 | 104 | 3714846 | 104 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:04 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4423 | 21.8121 | 4912393 | 105 | 3714847 | 105 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:05 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4423 | 21.8121 | 4912395 | 101 | 3714849 | 101 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:06 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4517 | 21.8027 | 4912397 | 106 | 3714851 | 106 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:07 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4517 | 21.7933 | 4912399 | 107 | 3714853 | 107 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:08 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4517 | 21.7838 | 4912401 | 103 | 3714855 | 103 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:09 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4799 | 21.8027 | 4912402 | 105 | 3714856 | 105 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:10 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4611 | 21.7933 | 4912404 | 102 | 3714858 | 102 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:11 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4611 | 21.7933 | 4912406 | 179 | 3714860 | 179 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:12 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4611 | 21.7838 | 4912410 | 169 | 3714864 | 169 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:13 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4517 | 21.7462 | 4912412 | 172 | 3714866 | 172 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:14 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4517 | 21.7556 | 4912415 | 177 | 3714869 | 177 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:15 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4517 | 21.7838 | 4912418 | 146 | 3714872 | 146 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:16 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4423 | 21.7838 | 4912420 | 145 | 3714874 | 145 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:17 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4329 | 21.7651 | 4912422 | 119 | 3714876 | 119 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:18 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4329 | 21.7462 | 4912424 | 110 | 3714878 | 110 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:19 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.4047 | 21.7368 | 4912426 | 112 | 3714880 | 112 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:20 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.3859 | 21.7651 | 4912428 | 116 | 3714882 | 116 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:21 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.367 | 21.7556 | 4912430 | 119 | 3714884 | 119 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:22 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.3576 | 21.7462 | 4912432 | 108 | 3714886 | 108 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:23 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.3482 | 21.7462 | 4912434 | 103 | 3714888 | 103 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:24 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.3388 | 21.7368 | 4912435 | 107 | 3714889 | 107 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:25 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.32 | 21.7462 | 4912437 | 109 | 3714891 | 109 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:26 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.3106 | 21.7368 | 4912439 | 140 | 3714893 | 140 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:27 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.32 | 21.7556 | 4912441 | 127 | 3714895 | 127 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:28 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.3106 | 21.7462 | 4912443 | 103 | 3714897 | 103 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:29 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.3012 | 21.7462 | 4912445 | 102 | 3714899 | 102 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:30 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.3012 | 21.6898 | 4912446 | 94 | 3714900 | 94 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:31 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.2918 | 21.6992 | 4912449 | 152 | 3714903 | 152 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:32 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.2918 | 21.6992 | 4912451 | 156 | 3714905 | 156 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:33 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.2918 | 21.6898 | 4912454 | 155 | 3714908 | 155 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:34 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.3012 | 21.6992 | 4912456 | 162 | 3714910 | 162 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:35 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.2918 | 21.671 | 4912459 | 156 | 3714913 | 156 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:36 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.2918 | 21.6616 | 4912462 | 216 | 3714916 | 216 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:37 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.273 | 21.6428 | 4912466 | 211 | 3714920 | 211 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:38 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.273 | 21.6522 | 4912469 | 208 | 3714923 | 208 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:39 | 1179146 | 0 | 0 | 1179146 | 0 | -2 | -4 | 19.273 | 21.671 | 4912473 | 212 | 3714927 | 212 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:40 | 1179146 | 0 | 0 | 1179146 | 0 | -1 | -2 | 19.273 | 21.6522 | 4912476 | 209 | 3714930 | 209 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:41 | 1179146 | 0 | 0 | 1179146 | 0 | -1 | -2 | 19.273 | 21.6522 | 4912480 | 213 | 3714934 | 213 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:42 | 1179146 | 0 | 0 | 1179146 | 0 | -1 | -2 | 19.273 | 21.6522 | 4912483 | 184 | 3714937 | 184 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:43 | 1179146 | 0 | 0 | 1179146 | 0 | -1 | -2 | 19.2918 | 21.6428 | 4912486 | 176 | 3714940 | 176 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:44 | 1179146 | 0 | 0 | 1179146 | 0 | -1 | -2 | 19.273 | 21.624 | 4912489 | 171 | 3714943 | 171 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:45 | 1179146 | 0 | 0 | 1179146 | 0 | -1 | -2 | 19.2918 | 21.6052 | 4912491 | 169 | 3714945 | 169 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 191890 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189914 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:46 | 1179146 | 0 | 0 | 1179146 | 0 | -1 | -2 | 19.273 | 21.6146 | 4912494 | 161 | 3714948 | 161 | 18400 | 0 | 0 | 188675 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186938 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 186499 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0.036 | 191890 | 0 | 100 | 0.05 | -0.02 | -0.02 | -0.02 | -0.02 | -0.03 | -0.02 | -0.02 | 0 | -0.03 | 0.05 | -0.01 | 0.02 | 189914 | 0 | 100 | 0.05 | -0.02 | -0.02 | -0.02 | -0.03 | -0.02 | -0.02 | -0.02 | -0.02 | -0.02 | 0.05 | -0.02 | 0 | 189706 | 0 | 100 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1
2025-11-27 05:47 | 1179146 | 0 | 0 | 1179146 | 0 | 0 | 0 | 19.2918 | 21.6146 | 4912496 | 97 | 3714950 | 97 | 18400 | 0 | 0.062 | 188675 | 0 | 100 | 0.07 | -0.02 | -0.04 | -0.03 | -0.03 | -0.04 | -0.04 | -0.03 | -0.03 | -0.05 | 0.07 | -0.03 | 0 | 186938 | 0 | 100 | 0.07 | -0.02 | -0.03 | -0.04 | -0.03 | -0.03 | -0.04 | -0.04 | -0.02 | -0.05 | 0.06 | -0.03 | 0 | 186499 | 0 | 100 | 0.02 | 0.01 | -0.01 | -0.01 | -0.01 | 0 | -0.01 | 0 | 0 | -0.01 | 0.03 | 0 | 0.066 | 191890 | 0.01 | 100 | 0.05 | -0.01 | -0.01 | -0.01 | -0.02 | -0.03 | -0.02 | -0.01 | -0.01 | -0.02 | 0.05 | 0.01 | 0.043 | 189914 | 0 | 100 | 0.05 | -0.01 | -0.03 | -0.02 | -0.03 | -0.03 | -0.02 | -0.02 | -0.02 | -0.02 | 0.06 | -0.03 | 0.044 | 189706 | 0 | 100 | 0.07 | -0.03 | -0.03 | -0.03 | -0.03 | -0.02 | -0.03 | -0.03 | -0.02 | -0.03 | 0.08 | -0.04 | 0 | 1
2025-11-27 05:48 | 1179146 | 0 | 0 | 1179146 | 0 | 0 | 0 | 19.2918 | 21.6052 | 4912497 | 88 | 3714951 | 88 | 18400 | 0 | 0.088 | 188675 | 0.01 | 100 | 0.07 | -0.02 | -0.03 | -0.03 | -0.03 | -0.04 | -0.04 | -0.03 | -0.03 | -0.06 | 0.07 | -0.03 | 0 | 186938 | 0 | 100 | 0.06 | -0.02 | -0.02 | -0.02 | -0.02 | -0.02 | -0.02 | -0.02 | -0.01 | -0.05 | 0.05 | -0.02 | 0.006 | 186499 | 0 | 100 | 0.03 | 0 | 0 | 0 | 0 | 0 | -0.01 | 0 | 0 | -0.01 | 0.03 | 0 | 0.085 | 191890 | 0.01 | 100 | 0.06 | -0.01 | -0.01 | -0.01 | -0.02 | -0.03 | -0.02 | -0.01 | -0.01 | -0.03 | 0.06 | 0 | 0.063 | 189914 | 0 | 100 | 0.06 | -0.02 | -0.02 | -0.03 | -0.02 | -0.03 | -0.02 | -0.02 | -0.02 | -0.02 | 0.06 | -0.03 | 0.061 | 189706 | 0.01 | 100 | 0.07 | -0.02 | -0.02 | -0.02 | -0.02 | -0.02 | -0.03 | -0.03 | -0.02 | -0.04 | 0.08 | -0.04 | 0 | 1
2025-11-27 05:49 | 1179146 | 0 | 0 | 1179146 | 0 | 0 | 0 | 19.2918 | 21.577 | 4912499 | 88 | 3714953 | 88 | 18400 | 0 | 0.1 | 188675 | 0.01 | 100 | 0.07 | -0.02 | -0.04 | -0.03 | -0.03 | -0.04 | -0.04 | -0.03 | -0.03 | -0.06 | 0.08 | -0.04 | 0 | 186938 | 0 | 100 | 0.06 | -0.02 | -0.02 | -0.02 | -0.03 | -0.02 | -0.03 | -0.03 | -0.01 | -0.04 | 0.06 | -0.02 | 0.023 | 186499 | 0 | 100 | 0.03 | 0.01 | 0.01 | 0 | 0 | 0.01 | -0.01 | 0 | 0 | -0.01 | 0.03 | 0 | 0.104 | 191890 | 0.01 | 100 | 0.07 | -0.01 | -0.02 | -0.01 | -0.02 | -0.03 | -0.02 | -0.01 | -0.01 | -0.03 | 0.06 | -0.01 | 0.08 | 189914 | 0 | 100 | 0.07 | -0.02 | -0.02 | -0.02 | -0.02 | -0.02 | -0.02 | -0.02 | -0.02 | -0.02 | 0.06 | -0.02 | 0.084 | 189706 | 0.01 | 100 | 0.07 | -0.01 | -0.02 | -0.02 | -0.02 | -0.02 | -0.03 | -0.02 | -0.02 | -0.03 | 0.08 | -0.03 | 0 | 1
2025-11-27 05:50 | 1179146 | 0 | 0 | 1179146 | 0 | 0 | 0 | 19.2918 | 21.6052 | 4912500 | 88 | 3714954 | 88 | 18400 | 0 | 0.121 | 188675 | 0.01 | 100 | 0.07 | -0.01 | -0.03 | -0.02 | -0.02 | -0.04 | -0.04 | -0.02 | -0.03 | -0.05 | 0.08 | -0.03 | 0 | 186938 | 0 | 100 | 0.07 | -0.01 | -0.02 | -0.02 | -0.01 | -0.03 | -0.03 | -0.02 | -0.01 | -0.04 | 0.07 | -0.02 | 0.043 | 186499 | 0 | 100 | 0.03 | 0 | 0 | 0 | 0 | 0.01 | -0.01 | 0 | -0.01 | -0.01 | 0.04 | -0.01 | 0.136 | 191890 | 0.01 | 100 | 0.07 | 0 | -0.01 | -0.01 | -0.02 | -0.03 | -0.02 | -0.01 | 0 | -0.02 | 0.06 | 0 | 0.112 | 189914 | 0 | 100 | 0.08 | -0.02 | -0.02 | -0.02 | -0.03 | -0.02 | -0.02 | -0.02 | -0.02 | -0.03 | 0.07 | -0.02 | 0.112 | 189706 | 0.01 | 100 | 0.08 | -0.02 | -0.02 | -0.02 | -0.02 | -0.03 | -0.03 | -0.02 | -0.02 | -0.04 | 0.09 | -0.03 | 0 | 1
2025-11-27 05:51 | 1179146 | 0 | 0 | 1179146 | 0 | 0 | 0 | 19.3012 | 21.5958 | 4912502 | 92 | 3714956 | 92 | 18400 | 0 | 0.146 | 188675 | 0.01 | 100 | 0.08 | -0.01 | -0.03 | -0.02 | -0.02 | -0.03 | -0.04 | -0.02 | -0.03 | -0.05 | 0.09 | -0.03 | 0.011 | 186938 | 0 | 100 | 0.08 | -0.02 | -0.02 | -0.02 | -0.02 | -0.02 | -0.03 | -0.02 | -0.01 | -0.05 | 0.07 | -0.02 | 0.069 | 186499 | 0 | 100 | 0.04 | 0.01 | 0 | 0 | 0 | 0.01 | 0 | 0.01 | 0 | -0.01 | 0.04 | 0 | 0.155 | 191890 | 0.01 | 100 | 0.08 | 0 | 0 | 0 | 0 | -0.02 | -0.01 | -0.01 | 0 | -0.01 | 0.07 | 0 | 0 | 189914 | 0 | 100 | 0.08 | -0.02 | -0.02 | -0.03 | -0.02 | -0.02 | -0.02 | -0.03 | -0.02 | -0.03 | 0.08 | -0.02 | 0.149 | 189706 | 0.01 | 100 | 0.08 | -0.01 | -0.01 | -0.01 | -0.02 | -0.02 | -0.02 | -0.01 | -0.01 | -0.03 | 0.09 | -0.03 | 0 | 1
2025-11-27 05:52 | 1179146 | 0 | 0 | 1179146 | 0 | 1 | 2 | 19.3012 | 21.624 | 4912503 | 98 | 3714957 | 98 | 18400 | 0 | 0 | 188675 | 0.01 | 100 | 0.09 | 0 | -0.03 | -0.01 | 0 | -0.03 | -0.03 | -0.02 | -0.03 | -0.02 | 0.09 | -0.02 | 0.048 | 186938 | 0 | 100 | 0.09 | -0.01 | 0.01 | -0.02 | -0.01 | -0.02 | -0.03 | 0.01 | 0.01 | 0 | 0.08 | -0.01 | 0.108 | 186499 | 0 | 100 | 0.04 | 0.01 | 0.01 | 0 | 0 | 0.02 | 0 | 0 | 0 | -0.01 | 0.05 | 0 | 0.232 | 191890 | 0.02 | 100 | 0.08 | 0.01 | 0 | 0 | 0.01 | -0.01 | 0 | 0.02 | -0.01 | -0.01 | 0.08 | 0.02 | 0.188 | 189914 | 0.01 | 100 | 0.09 | -0.01 | -0.01 | -0.02 | -0.01 | -0.01 | -0.01 | -0.01 | -0.02 | -0.01 | 0.08 | -0.01 | 0.202 | 189706 | 0.01 | 100 | 0.09 | -0.01 | -0.01 | 0 | -0.01 | -0.01 | -0.02 | 0.01 | -0.01 | -0.02 | 0.1 | -0.01 | 0 | 1
2025-11-27 05:53 | 1179146 | 0 | 1 | 1179146 | 1 | 1 | 2 | 19.3012 | 21.6522 | 4912505 | 99 | 3714959 | 98 | 18400 | 0 | 0.237 | 188675 | 0.02 | 100 | 0.09 | 0 | -0.01 | 0 | 0 | -0.02 | -0.04 | -0.02 | -0.02 | -0.01 | 0.1 | -0.02 | 0.094 | 186938 | 0 | 100 | 0.09 | -0.02 | 0.01 | -0.02 | 0.01 | -0.01 | -0.03 | 0.01 | 0.01 | 0 | 0.08 | 0 | 0.16 | 186499 | 0 | 100 | 0.05 | 0.02 | 0.01 | 0.01 | 0.01 | 0.02 | 0 | 0.01 | 0.01 | 0 | 0.06 | 0.02 | 0.298 | 191890 | 0.02 | 100 | 0.09 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | 0 | 0.02 | -0.01 | -0.01 | 0.09 | 0.03 | 0.261 | 189914 | 0.01 | 100 | 0.1 | 0 | -0.01 | -0.01 | -0.01 | -0.01 | -0.01 | -0.02 | 0 | -0.02 | 0.1 | -0.01 | 0.258 | 189706 | 0.02 | 100 | 0.1 | 0 | 0 | 0.01 | 0.01 | -0.01 | -0.01 | 0 | 0 | -0.01 | 0.11 | 0.01 | 0.98094 | 1
2025-11-27 05:54 | 1179146 | 0 | 1 | 1179146 | 1 | 2 | 4 | 19.3106 | 21.6052 | 4912507 | 102 | 3714961 | 101 | 18400 | 0 | 0.302 | 188675 | 0.02 | 100 | 0.1 | 0.01 | 0 | 0.01 | 0.02 | -0.01 | -0.03 | -0.01 | -0.02 | 0 | 0.11 | 0 | 0.154 | 186938 | 0.01 | 100 | 0.1 | -0.02 | 0.01 | -0.01 | 0.02 | -0.01 | -0.02 | 0.03 | 0.01 | 0 | 0.1 | 0 | 0.218 | 186499 | 0.01 | 100 | 0.06 | 0.03 | 0.02 | 0.01 | 0.02 | 0.03 | 0.01 | 0.02 | 0.02 | 0 | 0.06 | 0.02 | 0.37 | 191890 | 0.03 | 100 | 0.11 | 0.02 | 0.02 | 0.02 | 0.02 | 0.01 | 0.01 | 0.03 | 0 | -0.01 | 0.1 | 0.04 | 0.335 | 189914 | 0.02 | 100 | 0.11 | 0 | 0 | 0 | 0 | 0 | 0.01 | -0.01 | 0 | 0 | 0.11 | 0 | 0.331 | 189706 | 0.02 | 100 | 0.11 | 0.01 | 0.01 | 0.01 | 0.01 | 0 | -0.01 | 0.01 | 0.01 | -0.01 | 0.13 | 0.01 | 0.98097 | 1
2025-11-27 05:55 | 1179146 | 0 | 2 | 1179146 | 2 | 3 | 6 | 19.3106 | 21.6146 | 4912508 | 101 | 3714962 | 99 | 18400 | 0 | 0.354 | 188675 | 0.03 | 100 | 0.11 | 0.02 | 0 | 0.01 | 0.02 | -0.01 | -0.02 | -0.01 | -0.01 | 0 | 0.12 | 0 | 0.213 | 186938 | 0.01 | 100 | 0.11 | -0.01 | 0.01 | -0.01 | 0.02 | -0.01 | -0.01 | 0.02 | 0.02 | 0 | 0.11 | 0.01 | 0.263 | 186499 | 0.01 | 100 | 0.06 | 0.03 | 0.02 | 0.01 | 0.03 | 0.03 | 0.01 | 0.03 | 0.02 | 0 | 0.07 | 0.03 | 0.465 | 191890 | 0.03 | 100 | 0.12 | 0.03 | 0.02 | 0.02 | 0.03 | 0.01 | 0.02 | 0.03 | 0.01 | 0.01 | 0.11 | 0.04 | 0.404 | 189914 | 0.02 | 100 | 0.12 | 0.02 | 0.01 | 0.01 | 0.01 | 0.01 | 0.02 | 0.01 | 0.02 | 0.01 | 0.11 | 0.02 | 0.41 | 189706 | 0.03 | 100 | 0.12 | 0.01 | 0.01 | 0.02 | 0.02 | 0.01 | 0 | 0.02 | 0.02 | 0 | 0.13 | 0.02 | 1.9619 | 1
2025-11-27 05:56 | 1179146 | 0 | 2 | 1179146 | 2 | 4 | 8 | 19.3106 | 21.5958 | 4912510 | 98 | 3714964 | 96 | 18400 | 0 | 0.442 | 188675 | 0.03 | 100 | 0.13 | 0.02 | 0 | 0.02 | 0.02 | 0 | -0.01 | 0 | -0.01 | 0 | 0.13 | 0.02 | 0.297 | 186938 | 0.01 | 100 | 0.12 | -0.01 | 0.02 | 0 | 0.03 | 0 | 0 | 0.03 | 0.04 | 0.01 | 0.12 | 0.01 | 0.348 | 186499 | 0.02 | 100 | 0.08 | 0.03 | 0.03 | 0.02 | 0.02 | 0.04 | 0.02 | 0.03 | 0.02 | 0 | 0.09 | 0.03 | 0.559 | 191890 | 0.04 | 100 | 0.13 | 0.05 | 0.03 | 0.03 | 0.04 | 0.02 | 0.02 | 0.05 | 0.02 | 0.02 | 0.13 | 0.05 | 0.488 | 189914 | 0.03 | 100 | 0.13 | 0.03 | 0.02 | 0.02 | 0.02 | 0.02 | 0.03 | 0.02 | 0.02 | 0 | 0.12 | 0.03 | 0.502 | 189706 | 0.03 | 100 | 0.14 | 0.02 | 0.02 | 0.02 | 0.03 | 0.01 | 0.01 | 0.03 | 0.03 | 0.01 | 0.15 | 0.03 | 1.9619 | 1
2025-11-27 05:57 | 1179146 | 0 | 3 | 1179146 | 3 | 5 | 10 | 19.3106 | 21.5958 | 4912512 | 152 | 3714966 | 149 | 18400 | 0 | 0.542 | 188675 | 0.04 | 100 | 0.14 | 0.03 | 0.01 | 0.03 | 0.03 | 0.01 | -0.01 | 0 | 0 | 0.02 | 0.14 | 0.02 | 0.384 | 186938 | 0.02 | 100 | 0.14 | 0 | 0.03 | 0 | 0.04 | 0.01 | 0 | 0.04 | 0.05 | 0.02 | 0.13 | 0.03 | 0.431 | 186499 | 0.02 | 100 | 0.09 | 0.05 | 0.04 | 0.03 | 0.04 | 0.04 | 0.02 | 0.03 | 0.04 | 0.02 | 0.1 | 0.04 | 0.652 | 191890 | 0.05 | 100 | 0.14 | 0.05 | 0.05 | 0.04 | 0.05 | 0.03 | 0.04 | 0.06 | 0.04 | 0.03 | 0.14 | 0.07 | 0.58 | 189914 | 0.04 | 100 | 0.15 | 0.03 | 0.03 | 0.02 | 0.02 | 0.03 | 0.04 | 0.01 | 0.03 | 0.02 | 0.14 | 0 | 0.611 | 189706 | 0.04 | 100 | 0.15 | 0.04 | 0.03 | 0.04 | 0.04 | 0.02 | 0.02 | 0.04 | 0.03 | 0.02 | 0.16 | 0.03 | 2.9429 | 1
2025-11-27 05:58 | 1179146 | 0 | 3 | 1179146 | 3 | 6 | 12 | 19.32 | 21.6052 | 4912515 | 125 | 3714969 | 122 | 18400 | 0 | 0.633 | 188675 | 0.05 | 100 | 0.15 | 0.05 | 0.02 | 0.04 | 0.05 | 0.02 | 0 | 0.02 | 0.01 | 0.03 | 0.15 | 0.04 | 0.481 | 186938 | 0.03 | 100 | 0.14 | 0.02 | 0.05 | 0.02 | 0.05 | 0.02 | 0.02 | 0.06 | 0.06 | 0.03 | 0.14 | 0.04 | 0.535 | 186499 | 0.03 | 100 | 0.1 | 0.06 | 0.05 | 0.03 | 0.05 | 0.05 | 0.03 | 0.05 | 0.04 | 0.02 | 0.11 | 0.05 | 0.777 | 191890 | 0.06 | 100 | 0.16 | 0.07 | 0.06 | 0.05 | 0.06 | 0.05 | 0.05 | 0.07 | 0.05 | 0.05 | 0.15 | 0.08 | 0.696 | 189914 | 0.05 | 100 | 0.16 | 0.05 | 0.04 | 0.04 | 0.04 | 0.04 | 0.05 | 0.03 | 0.04 | 0.03 | 0.15 | 0.04 | 0.73 | 189706 | 0.06 | 100 | 0.16 | 0.04 | 0.04 | 0.05 | 0.05 | 0.04 | 0.04 | 0.06 | 0.05 | 0.04 | 0.17 | 0.05 | 2.943 | 1
2025-11-27 05:59 | 1179146 | 0 | 4 | 1179146 | 4 | 7 | 14 | 19.32 | 21.5958 | 4912517 | 130 | 3714971 | 126 | 18400 | 0 | 0.751 | 188675 | 0.06 | 100 | 0.16 | 0.06 | 0.04 | 0.05 | 0.06 | 0.03 | 0.02 | 0.04 | 0.02 | 0.04 | 0.17 | 0.05 | 0.6 | 186938 | 0.04 | 100 | 0.16 | 0.02 | 0.05 | 0.03 | 0.06 | 0.03 | 0.03 | 0.07 | 0.07 | 0.05 | 0.16 | 0.05 | 0.643 | 186499 | 0.04 | 100 | 0.11 | 0.07 | 0.06 | 0.05 | 0.06 | 0.08 | 0.06 | 0.06 | 0.06 | 0.04 | 0.12 | 0.06 | 0.905 | 191890 | 0.08 | 100 | 0.17 | 0.09 | 0.07 | 0.07 | 0.08 | 0.07 | 0.07 | 0.08 | 0.07 | 0.06 | 0.16 | 0.1 | 0.841 | 189914 | 0.06 | 100 | 0.18 | 0.06 | 0.06 | 0.05 | 0.05 | 0.05 | 0.07 | 0.05 | 0.06 | 0.05 | 0.17 | 0.05 | 0.849 | 189706 | 0.07 | 100 | 0.17 | 0.06 | 0.05 | 0.06 | 0.05 | 0.06 | 0.05 | 0.07 | 0.06 | 0.05 | 0.18 | 0.05 | 3.924 | 1
2025-11-27 06:00 | 1179146 | 0 | 5 | 1179146 | 5 | 9 | 18 | 19.32 | 21.6052 | 4912519 | 123 | 3714973 | 118 | 18400 | 0 | 0.877 | 188675 | 0.08 | 100 | 0.18 | 0.08 | 0.06 | 0.06 | 0.07 | 0.06 | 0.03 | 0.05 | 0.04 | 0.05 | 0.18 | 0.05 | 0.713 | 186938 | 0.05 | 100 | 0.18 | 0.03 | 0.07 | 0.04 | 0.07 | 0.04 | 0.04 | 0.08 | 0.08 | 0.05 | 0.17 | 0.06 | 0.748 | 186499 | 0.05 | 100 | 0.13 | 0.08 | 0.07 | 0.06 | 0.07 | 0.08 | 0.07 | 0.08 | 0.07 | 0.04 | 0.14 | 0.09 | 1.057 | 191890 | 0.09 | 100 | 0.19 | 0.1 | 0.09 | 0.08 | 0.11 | 0.1 | 0.09 | 0.1 | 0.08 | 0.08 | 0.18 | 0.12 | 0.941 | 189914 | 0.08 | 100 | 0.19 | 0.09 | 0.08 | 0.07 | 0.07 | 0.06 | 0.07 | 0.06 | 0.07 | 0.06 | 0.17 | 0.06 | 0.985 | 189706 | 0.08 | 100 | 0.19 | 0.09 | 0.07 | 0.07 | 0.08 | 0.07 | 0.09 | 0.08 | 0.09 | 0.06 | 0.2 | 0.09 | 4.905 | 1
2025-11-27 06:01 | 1179146 | 0 | 6 | 1179146 | 6 | 10 | 20 | 19.32 | 21.6052 | 4912521 | 109 | 3714975 | 103 | 18400 | 0 | 1.022 | 188675 | 0.09 | 100 | 0.19 | 0.09 | 0.06 | 0.08 | 0.09 | 0.07 | 0.04 | 0.06 | 0.05 | 0.05 | 0.2 | 0.08 | 0.832 | 186938 | 0.06 | 100 | 0.19 | 0.06 | 0.08 | 0.06 | 0.09 | 0.06 | 0.06 | 0.09 | 0.1 | 0.07 | 0.19 | 0.08 | 0.887 | 186499 | 0.06 | 100 | 0.14 | 0.1 | 0.09 | 0.07 | 0.09 | 0.1 | 0.09 | 0.09 | 0.08 | 0.06 | 0.15 | 0.09 | 1.144 | 191890 | 0.11 | 100 | 0.22 | 0.11 | 0.1 | 0.1 | 0.11 | 0.09 | 0.1 | 0.11 | 0.11 | 0.08 | 0.21 | 0.12 | 1.04 | 189914 | 0.09 | 100 | 0.22 | 0.09 | 0.08 | 0.08 | 0.07 | 0.07 | 0.1 | 0.07 | 0.09 | 0.07 | 0.16 | 0.04 | 1.123 | 189706 | 0.1 | 100 | 0.21 | 0.11 | 0.09 | 0.09 | 0.1 | 0.09 | 0.09 | 0.11 | 0.1 | 0.08 | 0.21 | 0.1 | 5.886 | 1
2025-11-27 06:02 | 1179146 | 0 | 6 | 1179146 | 7 | 12 | 24 | 19.32 | 21.5676 | 4912523 | 118 | 3714977 | 112 | 18400 | 0 | 1.063 | 188675 | 0.11 | 100 | 0.17 | 0.05 | 0.08 | 0.1 | 0.09 | 0.08 | 0.06 | 0.06 | 0.07 | 0.08 | 0.22 | 0.08 | 1.012 | 186938 | 0.07 | 100 | 0.21 | 0.07 | 0.07 | 0.07 | 0.1 | 0.07 | 0.07 | 0.1 | 0.11 | 0.06 | 0.21 | 0.1 | 0.987 | 186499 | 0.08 | 100 | 0.16 | 0.1 | 0.09 | 0.08 | 0.1 | 0.11 | 0.09 | 0.1 | 0.09 | 0.08 | 0.17 | 0.09 | 1.36 | 191890 | 0.13 | 100 | 0.23 | 0.13 | 0.13 | 0.14 | 0.13 | 0.11 | 0.12 | 0.12 | 0.13 | 0.11 | 0.22 | 0.16 | 1.24 | 189914 | 0.11 | 100 | 0.23 | 0.1 | 0.1 | 0.11 | 0.1 | 0.09 | 0.1 | 0.1 | 0.09 | 0.09 | 0.21 | 0.12 | 1.28 | 189706 | 0.12 | 100 | 0.23 | 0.11 | 0.11 | 0.1 | 0.1 | 0.08 | 0.08 | 0.1 | 0.1 | 0.07 | 0.24 | 0.11 | 5.886 | 1
2025-11-27 06:03 | 1179146 | 0 | 7 | 1179146 | 7 | 13 | 26 | 19.3388 | 21.5676 | 4912525 | 174 | 3714979 | 167 | 18400 | 0 | 1.283 | 188675 | 0.13 | 100 | 0.22 | 0.14 | 0.1 | 0.12 | 0.12 | 0.1 | 0.11 | 0.09 | 0.11 | 0.1 | 0.24 | 0.11 | 1.106 | 186938 | 0.09 | 100 | 0.22 | 0.1 | 0.1 | 0.09 | 0.11 | 0.11 | 0.1 | 0.12 | 0.11 | 0.09 | 0.21 | 0.12 | 1.112 | 186499 | 0.1 | 100 | 0.15 | 0.06 | 0.11 | 0.1 | 0.1 | 0.13 | 0.11 | 0.12 | 0.11 | 0.1 | 0.19 | 0.11 | 1.525 | 191890 | 0.16 | 100 | 0.25 | 0.16 | 0.16 | 0.15 | 0.16 | 0.14 | 0.15 | 0.15 | 0.15 | 0.13 | 0.24 | 0.19 | 1.389 | 189914 | 0.13 | 100 | 0.25 | 0.12 | 0.11 | 0.13 | 0.11 | 0.11 | 0.12 | 0.12 | 0.11 | 0.11 | 0.23 | 0.07 | 1.429 | 189707 | 0.14 | 100 | 0.25 | 0.13 | 0.12 | 0.12 | 0.12 | 0.11 | 0.11 | 0.12 | 0.13 | 0.09 | 0.25 | 0.16 | 6.8674 | 1
2025-11-27 06:04 | 1179146 | 0 | 8 | 1179146 | 8 | 15 | 30 | 19.3482 | 21.577 | 4912527 | 161 | 3714981 | 153 | 18400 | 0 | 1.445 | 188675 | 0.15 | 100 | 0.24 | 0.15 | 0.13 | 0.14 | 0.14 | 0.13 | 0.14 | 0.11 | 0.12 | 0.11 | 0.25 | 0.12 | 1.269 | 186938 | 0.11 | 100 | 0.24 | 0.11 | 0.12 | 0.09 | 0.12 | 0.12 | 0.11 | 0.14 | 0.12 | 0.11 | 0.24 | 0.13 | 1.261 | 186499 | 0.12 | 100 | 0.16 | 0.1 | 0.13 | 0.12 | 0.12 | 0.14 | 0.13 | 0.13 | 0.13 | 0.11 | 0.21 | 0.13 | 1.705 | 191890 | 0.18 | 100 | 0.27 | 0.17 | 0.18 | 0.16 | 0.17 | 0.15 | 0.18 | 0.17 | 0.17 | 0.15 | 0.27 | 0.2 | 1.546 | 189914 | 0.16 | 100 | 0.27 | 0.14 | 0.13 | 0.14 | 0.13 | 0.13 | 0.14 | 0.13 | 0.13 | 0.12 | 0.22 | 0.07 | 1.601 | 189707 | 0.17 | 100 | 0.27 | 0.14 | 0.14 | 0.13 | 0.14 | 0.12 | 0.11 | 0.14 | 0.14 | 0.11 | 0.28 | 0.15 | 7.8487 | 1
2025-11-27 06:05 | 1179147 | 0 | 9 | 1179147 | 9 | 17 | 34 | 19.367 | 21.6052 | 4912531 | 164 | 3714984 | 155 | 18400 | 0 | 1.577 | 188675 | 0.18 | 100 | 0.25 | 0.14 | 0.14 | 0.14 | 0.16 | 0.13 | 0.14 | 0.13 | 0.13 | 0.11 | 0.27 | 0.13 | 1.418 | 186938 | 0.13 | 100 | 0.26 | 0.12 | 0.11 | 0.12 | 0.13 | 0.14 | 0.13 | 0.14 | 0.12 | 0.12 | 0.25 | 0.14 | 1.423 | 186499 | 0.14 | 100 | 0.18 | 0.1 | 0.15 | 0.14 | 0.13 | 0.16 | 0.12 | 0.15 | 0.15 | 0.13 | 0.23 | 0.14 | 1.872 | 191890 | 0.21 | 100 | 0.29 | 0.2 | 0.19 | 0.18 | 0.2 | 0.17 | 0.18 | 0.19 | 0.19 | 0.15 | 0.29 | 0.21 | 1.707 | 189914 | 0.18 | 100 | 0.3 | 0.16 | 0.16 | 0.15 | 0.15 | 0.15 | 0.16 | 0.15 | 0.15 | 0.15 | 0.27 | 0.19 | 1.756 | 189707 | 0.2 | 100 | 0.29 | 0.17 | 0.14 | 0.15 | 0.16 | 0.13 | 0.14 | 0.16 | 0.17 | 0.12 | 0.3 | 0.15 | 8.8304 | 1
2025-11-27 06:06 | 1179147 | 1 | 10 | 1179147 | 10 | 18 | 36 | 19.4047 | 21.5676 | 4912534 | 165 | 3714987 | 155 | 18400 | 0 | 1.698 | 188675 | 0.21 | 100 | 0.25 | 0.15 | 0.15 | 0.15 | 0.16 | 0.15 | 0.14 | 0.14 | 0.15 | 0.12 | 0.29 | 0.16 | 1.552 | 186938 | 0.16 | 100 | 0.28 | 0.13 | 0.14 | 0.12 | 0.15 | 0.15 | 0.14 | 0.15 | 0.14 | 0.12 | 0.27 | 0.16 | 1.594 | 186499 | 0.17 | 100 | 0.23 | 0.16 | 0.15 | 0.15 | 0.15 | 0.17 | 0.14 | 0.16 | 0.16 | 0.15 | 0.25 | 0.17 | 2.046 | 191890 | 0.25 | 100 | 0.32 | 0.22 | 0.2 | 0.2 | 0.2 | 0.19 | 0.2 | 0.21 | 0.21 | 0.17 | 0.31 | 0.23 | 1.919 | 189914 | 0.22 | 100 | 0.31 | 0.18 | 0.18 | 0.19 | 0.18 | 0.18 | 0.19 | 0.16 | 0.17 | 0.17 | 0.3 | 0.18 | 1.912 | 189707 | 0.23 | 100 | 0.31 | 0.18 | 0.16 | 0.16 | 0.18 | 0.16 | 0.17 | 0.18 | 0.19 | 0.14 | 0.31 | 0.18 | 9.8128 | 1
2025-11-27 06:07 | 1179147 | 1 | 11 | 1179147 | 11 | 20 | 40 | 19.4141 | 21.577 | 4912536 | 162 | 3714989 | 151 | 18400 | 0 | 1.839 | 188675 | 0.24 | 100 | 0.25 | 0.12 | 0.19 | 0.15 | 0.17 | 0.17 | 0.15 | 0.16 | 0.17 | 0.14 | 0.31 | 0.17 | 1.699 | 186938 | 0.19 | 100 | 0.3 | 0.14 | 0.16 | 0.13 | 0.16 | 0.18 | 0.16 | 0.18 | 0.17 | 0.15 | 0.29 | 0.18 | 1.757 | 186499 | 0.19 | 100 | 0.25 | 0.18 | 0.18 | 0.17 | 0.18 | 0.19 | 0.17 | 0.19 | 0.16 | 0.18 | 0.26 | 0.17 | 2.226 | 191890 | 0.28 | 100 | 0.34 | 0.23 | 0.23 | 0.22 | 0.24 | 0.21 | 0.25 | 0.22 | 0.23 | 0.2 | 0.33 | 0.26 | 2.07 | 189914 | 0.25 | 100 | 0.33 | 0.22 | 0.19 | 0.21 | 0.19 | 0.21 | 0.2 | 0.21 | 0.19 | 0.18 | 0.33 | 0.18 | 2.06 | 189707 | 0.26 | 100 | 0.33 | 0.21 | 0.2 | 0.19 | 0.19 | 0.16 | 0.17 | 0.2 | 0.21 | 0.15 | 0.33 | 0.2 | 10.7944 | 1
2025-11-27 06:08 | 1179147 | 1 | 12 | 1179147 | 12 | 22 | 44 | 19.4517 | 21.624 | 4912539 | 134 | 3714992 | 122 | 18400 | 0 | 2.05 | 188675 | 0.27 | 100 | 0.32 | 0.21 | 0.21 | 0.19 | 0.19 | 0.19 | 0.18 | 0.18 | 0.18 | 0.16 | 0.33 | 0.18 | 1.846 | 186938 | 0.22 | 100 | 0.31 | 0.16 | 0.17 | 0.15 | 0.17 | 0.18 | 0.17 | 0.16 | 0.18 | 0.13 | 0.3 | 0.2 | 1.892 | 186499 | 0.22 | 100 | 0.27 | 0.21 | 0.19 | 0.19 | 0.18 | 0.2 | 0.2 | 0.21 | 0.2 | 0.18 | 0.28 | 0.2 | 2.387 | 191890 | 0.32 | 100 | 0.36 | 0.26 | 0.25 | 0.25 | 0.24 | 0.22 | 0.23 | 0.24 | 0.25 | 0.2 | 0.35 | 0.27 | 2.211 | 189914 | 0.28 | 100 | 0.35 | 0.22 | 0.22 | 0.23 | 0.22 | 0.19 | 0.23 | 0.23 | 0.21 | 0.2 | 0.35 | 0.23 | 2.243 | 189707 | 0.3 | 100 | 0.34 | 0.22 | 0.21 | 0.21 | 0.22 | 0.2 | 0.2 | 0.22 | 0.22 | 0.18 | 0.35 | 0.22 | 11.7772 | 1
2025-11-27 06:09 | 1179147 | 1 | 13 | 1179147 | 13 | 24 | 48 | 19.4799 | 21.6616 | 4912541 | 139 | 3714994 | 126 | 18400 | 0 | 2.195 | 188675 | 0.3 | 100 | 0.34 | 0.23 | 0.21 | 0.18 | 0.21 | 0.2 | 0.19 | 0.19 | 0.2 | 0.18 | 0.35 | 0.2 | 2.009 | 186938 | 0.25 | 100 | 0.32 | 0.18 | 0.19 | 0.17 | 0.2 | 0.2 | 0.19 | 0.21 | 0.2 | 0.18 | 0.32 | 0.22 | 2.041 | 186499 | 0.26 | 100 | 0.29 | 0.22 | 0.2 | 0.2 | 0.21 | 0.22 | 0.21 | 0.21 | 0.21 | 0.2 | 0.3 | 0.22 | 2.556 | 191890 | 0.36 | 100 | 0.37 | 0.28 | 0.27 | 0.26 | 0.29 | 0.23 | 0.27 | 0.26 | 0.24 | 0.21 | 0.37 | 0.29 | 2.421 | 189914 | 0.32 | 100 | 0.37 | 0.24 | 0.22 | 0.27 | 0.23 | 0.24 | 0.22 | 0.25 | 0.22 | 0.23 | 0.37 | 0.25 | 2.427 | 189707 | 0.33 | 100 | 0.37 | 0.25 | 0.24 | 0.22 | 0.23 | 0.21 | 0.22 | 0.23 | 0.24 | 0.18 | 0.37 | 0.23 | 12.7598 | 1
2025-11-27 06:10 | 1179148 | 1 | 14 | 1179148 | 14 | 25 | 50 | 19.5081 | 21.6428 | 4912544 | 131 | 3714996 | 117 | 18400 | 0 | 2.35 | 188676 | 0.34 | 100 | 0.36 | 0.25 | 0.23 | 0.21 | 0.23 | 0.23 | 0.2 | 0.2 | 0.21 | 0.21 | 0.37 | 0.21 | 2.149 | 186938 | 0.28 | 100 | 0.35 | 0.21 | 0.21 | 0.2 | 0.21 | 0.21 | 0.2 | 0.23 | 0.21 | 0.2 | 0.35 | 0.23 | 2.189 | 186499 | 0.29 | 100 | 0.3 | 0.24 | 0.23 | 0.22 | 0.22 | 0.24 | 0.23 | 0.24 | 0.24 | 0.21 | 0.31 | 0.22 | 2.743 | 191890 | 0.41 | 100 | 0.4 | 0.3 | 0.27 | 0.29 | 0.3 | 0.28 | 0.3 | 0.29 | 0.3 | 0.25 | 0.39 | 0.31 | 2.578 | 189914 | 0.37 | 100 | 0.39 | 0.26 | 0.26 | 0.29 | 0.26 | 0.25 | 0.26 | 0.27 | 0.26 | 0.25 | 0.39 | 0.27 | 2.593 | 189707 | 0.38 | 100 | 0.39 | 0.26 | 0.27 | 0.23 | 0.24 | 0.23 | 0.24 | 0.25 | 0.27 | 0.21 | 0.4 | 0.25 | 13.7426 | 1
2025-11-27 06:11 | 1179148 | 2 | 15 | 1179148 | 15 | 27 | 54 | 19.5457 | 21.6522 | 4912546 | 130 | 3714998 | 115 | 18400 | 0 | 2.518 | 188676 | 0.38 | 100 | 0.38 | 0.27 | 0.24 | 0.25 | 0.25 | 0.25 | 0.22 | 0.23 | 0.24 | 0.22 | 0.39 | 0.24 | 2.304 | 186938 | 0.32 | 100 | 0.37 | 0.23 | 0.21 | 0.21 | 0.23 | 0.23 | 0.22 | 0.27 | 0.22 | 0.2 | 0.37 | 0.25 | 2.331 | 186499 | 0.33 | 100 | 0.32 | 0.25 | 0.23 | 0.24 | 0.23 | 0.25 | 0.23 | 0.25 | 0.25 | 0.22 | 0.34 | 0.24 | 2.914 | 191890 | 0.45 | 100 | 0.42 | 0.33 | 0.31 | 0.31 | 0.33 | 0.3 | 0.31 | 0.3 | 0.32 | 0.24 | 0.41 | 0.32 | 2.74 | 189915 | 0.41 | 100 | 0.41 | 0.29 | 0.28 | 0.31 | 0.28 | 0.27 | 0.29 | 0.3 | 0.26 | 0.26 | 0.41 | 0.3 | 2.754 | 189707 | 0.42 | 100 | 0.41 | 0.29 | 0.27 | 0.24 | 0.25 | 0.25 | 0.23 | 0.27 | 0.28 | 0.22 | 0.41 | 0.28 | 14.7261 | 1
2025-11-27 06:12 | 1179148 | 2 | 16 | 1179148 | 17 | 29 | 58 | 19.5739 | 21.6898 | 4912548 | 129 | 3715000 | 113 | 18400 | 0 | 2.673 | 188676 | 0.42 | 100 | 0.4 | 0.29 | 0.26 | 0.26 | 0.26 | 0.27 | 0.26 | 0.24 | 0.25 | 0.23 | 0.41 | 0.27 | 2.475 | 186938 | 0.36 | 100 | 0.38 | 0.25 | 0.23 | 0.23 | 0.25 | 0.27 | 0.23 | 0.28 | 0.25 | 0.23 | 0.38 | 0.27 | 2.484 | 186499 | 0.37 | 100 | 0.34 | 0.28 | 0.25 | 0.26 | 0.25 | 0.27 | 0.23 | 0.27 | 0.26 | 0.2 | 0.35 | 0.25 | 3.104 | 191890 | 0.5 | 100 | 0.44 | 0.35 | 0.34 | 0.33 | 0.31 | 0.31 | 0.32 | 0.33 | 0.35 | 0.27 | 0.44 | 0.37 | 2.901 | 189915 | 0.45 | 100 | 0.42 | 0.31 | 0.28 | 0.33 | 0.3 | 0.3 | 0.31 | 0.29 | 0.3 | 0.29 | 0.44 | 0.3 | 2.897 | 189707 | 0.47 | 100 | 0.43 | 0.3 | 0.29 | 0.26 | 0.28 | 0.28 | 0.24 | 0.29 | 0.29 | 0.22 | 0.43 | 0.28 | 15.7093 | 1
2025-11-27 06:13 | 1179148 | 2 | 18 | 1179148 | 18 | 31 | 62 | 19.6021 | 21.6616 | 4912549 | 117 | 3715001 | 99 | 18400 | 0 | 2.851 | 188676 | 0.47 | 100 | 0.42 | 0.31 | 0.28 | 0.28 | 0.31 | 0.29 | 0.28 | 0.26 | 0.26 | 0.24 | 0.43 | 0.27 | 2.624 | 186938 | 0.4 | 100 | 0.4 | 0.26 | 0.25 | 0.26 | 0.28 | 0.27 | 0.26 | 0.3 | 0.26 | 0.26 | 0.4 | 0.28 | 2.62 | 186499 | 0.41 | 100 | 0.36 | 0.28 | 0.27 | 0.27 | 0.26 | 0.28 | 0.24 | 0.28 | 0.28 | 0.22 | 0.38 | 0.28 | 3.282 | 191891 | 0.56 | 100 | 0.47 | 0.37 | 0.34 | 0.34 | 0.35 | 0.32 | 0.35 | 0.35 | 0.36 | 0.3 | 0.46 | 0.39 | 3.126 | 189915 | 0.5 | 100 | 0.45 | 0.34 | 0.31 | 0.38 | 0.33 | 0.31 | 0.32 | 0.31 | 0.3 | 0.31 | 0.45 | 0.31 | 3.103 | 189707 | 0.52 | 100 | 0.45 | 0.33 | 0.31 | 0.31 | 0.3 | 0.29 | 0.3 | 0.32 | 0.33 | 0.25 | 0.46 | 0.31 | 17.6747 | 1
2025-11-27 06:14 | 1179149 | 2 | 19 | 1179149 | 19 | 33 | 66 | 19.6492 | 21.6898 | 4912552 | 140 | 3715003 | 121 | 18400 | 0 | 3.004 | 188676 | 0.52 | 100 | 0.44 | 0.33 | 0.3 | 0.32 | 0.3 | 0.3 | 0.3 | 0.28 | 0.28 | 0.26 | 0.46 | 0.3 | 2.786 | 186938 | 0.45 | 100 | 0.42 | 0.28 | 0.27 | 0.27 | 0.29 | 0.3 | 0.24 | 0.31 | 0.27 | 0.26 | 0.43 | 0.3 | 2.806 | 186499 | 0.46 | 100 | 0.37 | 0.31 | 0.29 | 0.28 | 0.3 | 0.31 | 0.29 | 0.31 | 0.3 | 0.26 | 0.39 | 0.31 | 3.461 | 191891 | 0.61 | 100 | 0.49 | 0.39 | 0.37 | 0.37 | 0.37 | 0.35 | 0.37 | 0.37 | 0.38 | 0.34 | 0.48 | 0.41 | 3.271 | 189915 | 0.56 | 100 | 0.48 | 0.37 | 0.32 | 0.31 | 0.34 | 0.32 | 0.34 | 0.34 | 0.33 | 0.33 | 0.48 | 0.34 | 3.315 | 189707 | 0.57 | 100 | 0.48 | 0.35 | 0.33 | 0.29 | 0.31 | 0.3 | 0.32 | 0.33 | 0.34 | 0.28 | 0.48 | 0.32 | 18.6595 | 1
2025-11-27 06:15 | 1179149 | 3 | 20 | 1179149 | 20 | 35 | 70 | 19.715 | 21.7086 | 4912554 | 139 | 3715005 | 119 | 18400 | 0 | 3.189 | 188676 | 0.57 | 100 | 0.46 | 0.35 | 0.32 | 0.33 | 0.35 | 0.33 | 0.33 | 0.3 | 0.3 | 0.26 | 0.47 | 0.32 | 2.954 | 186938 | 0.49 | 100 | 0.43 | 0.3 | 0.28 | 0.29 | 0.31 | 0.32 | 0.31 | 0.31 | 0.3 | 0.29 | 0.44 | 0.31 | 2.958 | 186499 | 0.5 | 100 | 0.4 | 0.33 | 0.31 | 0.3 | 0.29 | 0.34 | 0.28 | 0.33 | 0.32 | 0.26 | 0.41 | 0.33 | 3.689 | 191891 | 0.67 | 100 | 0.51 | 0.41 | 0.39 | 0.39 | 0.39 | 0.36 | 0.38 | 0.4 | 0.41 | 0.37 | 0.5 | 0.44 | 3.483 | 189915 | 0.61 | 100 | 0.5 | 0.38 | 0.35 | 0.39 | 0.37 | 0.34 | 0.37 | 0.37 | 0.34 | 0.35 | 0.5 | 0.36 | 3.509 | 189707 | 0.63 | 100 | 0.49 | 0.37 | 0.35 | 0.34 | 0.34 | 0.33 | 0.34 | 0.36 | 0.36 | 0.34 | 0.5 | 0.32 | 19.6459 | 1
2025-11-27 06:16 | 1179149 | 3 | 21 | 1179149 | 21 | 37 | 74 | 19.762 | 21.7368 | 4912556 | 135 | 3715007 | 114 | 18400 | 0 | 3.356 | 188676 | 0.62 | 100 | 0.48 | 0.37 | 0.34 | 0.34 | 0.36 | 0.34 | 0.33 | 0.32 | 0.32 | 0.32 | 0.49 | 0.35 | 3.113 | 186938 | 0.54 | 100 | 0.47 | 0.31 | 0.31 | 0.3 | 0.33 | 0.31 | 0.32 | 0.35 | 0.28 | 0.31 | 0.46 | 0.31 | 3.148 | 186499 | 0.55 | 100 | 0.42 | 0.34 | 0.34 | 0.32 | 0.33 | 0.34 | 0.31 | 0.34 | 0.34 | 0.29 | 0.44 | 0.34 | 3.696 | 191891 | 0.73 | 100 | 0.54 | 0.44 | 0.41 | 0.42 | 0.41 | 0.4 | 0.4 | 0.41 | 0.16 | 0.38 | 0.53 | 0.46 | 3.648 | 189915 | 0.68 | 100 | 0.53 | 0.4 | 0.38 | 0.37 | 0.38 | 0.39 | 0.38 | 0.38 | 0.38 | 0.37 | 0.53 | 0.38 | 3.707 | 189707 | 0.69 | 100 | 0.52 | 0.4 | 0.38 | 0.35 | 0.36 | 0.36 | 0.36 | 0.39 | 0.39 | 0.36 | 0.52 | 0.37 | 20.6315 | 1
2025-11-27 06:17 | 1179150 | 3 | 22 | 1179150 | 22 | 39 | 78 | 19.809 | 21.7651 | 4912559 | 130 | 3715009 | 108 | 18400 | 0 | 3.549 | 188676 | 0.68 | 100 | 0.5 | 0.39 | 0.36 | 0.37 | 0.37 | 0.36 | 0.36 | 0.35 | 0.34 | 0.35 | 0.51 | 0.37 | 3.281 | 186938 | 0.6 | 100 | 0.48 | 0.32 | 0.32 | 0.31 | 0.33 | 0.34 | 0.34 | 0.36 | 0.35 | 0.33 | 0.49 | 0.33 | 3.301 | 186499 | 0.61 | 100 | 0.44 | 0.36 | 0.35 | 0.35 | 0.32 | 0.36 | 0.34 | 0.36 | 0.35 | 0.29 | 0.46 | 0.36 | 4.004 | 191891 | 0.8 | 100 | 0.57 | 0.45 | 0.43 | 0.43 | 0.44 | 0.4 | 0.43 | 0.42 | 0.46 | 0.41 | 0.54 | 0.48 | 3.822 | 189915 | 0.74 | 100 | 0.55 | 0.43 | 0.36 | 0.41 | 0.4 | 0.34 | 0.41 | 0.4 | 0.38 | 0.39 | 0.55 | 0.41 | 3.777 | 189707 | 0.75 | 100 | 0.54 | 0.41 | 0.33 | 0.38 | 0.39 | 0.36 | 0.38 | 0.38 | 0.41 | 0.37 | 0.54 | 0.38 | 21.6173 | 1
2025-11-27 06:18 | 1179150 | 4 | 23 | 1179150 | 23 | 41 | 82 | 19.8749 | 21.8121 | 4912561 | 133 | 3715011 | 110 | 18400 | 0 | 3.688 | 188676 | 0.75 | 100 | 0.53 | 0.41 | 0.37 | 0.39 | 0.39 | 0.33 | 0.38 | 0.35 | 0.37 | 0.37 | 0.53 | 0.39 | 3.466 | 186939 | 0.66 | 100 | 0.5 | 0.35 | 0.36 | 0.35 | 0.37 | 0.37 | 0.36 | 0.38 | 0.37 | 0.35 | 0.5 | 0.35 | 3.503 | 186499 | 0.67 | 100 | 0.46 | 0.39 | 0.39 | 0.37 | 0.35 | 0.38 | 0.37 | 0.38 | 0.36 | 0.37 | 0.48 | 0.38 | 4.305 | 191891 | 0.87 | 100 | 0.59 | 0.48 | 0.46 | 0.45 | 0.45 | 0.43 | 0.46 | 0.45 | 0.46 | 0.44 | 0.56 | 0.5 | 4.08 | 189915 | 0.8 | 100 | 0.58 | 0.45 | 0.42 | 0.45 | 0.43 | 0.43 | 0.44 | 0.43 | 0.43 | 0.4 | 0.58 | 0.44 | 4.097 | 189707 | 0.82 | 100 | 0.57 | 0.44 | 0.41 | 0.39 | 0.39 | 0.39 | 0.4 | 0.42 | 0.42 | 0.4 | 0.56 | 0.4 | 22.6049 | 1
2025-11-27 06:19 | 1179150 | 4 | 24 | 1179151 | 24 | 43 | 86 | 19.9313 | 21.8309 | 4912562 | 127 | 3715012 | 103 | 18400 | 0 | 3.746 | 188676 | 0.81 | 100 | 0.55 | 0.44 | 0.23 | 0.41 | 0.4 | 0.37 | 0.4 | 0.39 | 0.38 | 0.39 | 0.56 | 0.4 | 3.62 | 186939 | 0.71 | 100 | 0.52 | 0.37 | 0.37 | 0.35 | 0.37 | 0.4 | 0.39 | 0.41 | 0.39 | 0.37 | 0.53 | 0.39 | 3.663 | 186500 | 0.73 | 100 | 0.48 | 0.4 | 0.39 | 0.38 | 0.35 | 0.41 | 0.39 | 0.4 | 0.4 | 0.39 | 0.5 | 0.4 | 4.478 | 191891 | 0.94 | 100 | 0.61 | 0.51 | 0.5 | 0.51 | 0.51 | 0.46 | 0.47 | 0.47 | 0.5 | 0.46 | 0.6 | 0.52 | 4.274 | 189915 | 0.87 | 100 | 0.59 | 0.47 | 0.45 | 0.47 | 0.45 | 0.46 | 0.48 | 0.46 | 0.44 | 0.43 | 0.6 | 0.45 | 4.302 | 189707 | 0.89 | 100 | 0.59 | 0.46 | 0.44 | 0.45 | 0.42 | 0.41 | 0.42 | 0.45 | 0.45 | 0.42 | 0.59 | 0.43 | 23.5922 | 1
2025-11-27 06:20 | 1179151 | 4 | 26 | 1179151 | 26 | 45 | 90 | 19.9971 | 21.8591 | 4912565 | 132 | 3715014 | 106 | 18400 | 0 | 4.102 | 188676 | 0.87 | 100 | 0.57 | 0.46 | 0.43 | 0.4 | 0.41 | 0.42 | 0.42 | 0.41 | 0.42 | 0.41 | 0.57 | 0.43 | 3.827 | 186939 | 0.77 | 100 | 0.54 | 0.38 | 0.4 | 0.38 | 0.4 | 0.42 | 0.41 | 0.42 | 0.41 | 0.4 | 0.55 | 0.4 | 3.863 | 186500 | 0.79 | 100 | 0.48 | 0.42 | 0.41 | 0.39 | 0.41 | 0.44 | 0.41 | 0.42 | 0.42 | 0.41 | 0.52 | 0.42 | 4.715 | 191891 | 1.02 | 100 | 0.64 | 0.53 | 0.53 | 0.5 | 0.54 | 0.48 | 0.5 | 0.5 | 0.51 | 0.48 | 0.62 | 0.54 | 4.498 | 189915 | 0.95 | 100 | 0.62 | 0.5 | 0.47 | 0.5 | 0.47 | 0.46 | 0.5 | 0.5 | 0.46 | 0.46 | 0.62 | 0.48 | 4.471 | 189707 | 0.96 | 100 | 0.61 | 0.48 | 0.46 | 0.42 | 0.45 | 0.43 | 0.44 | 0.46 | 0.49 | 0.43 | 0.61 | 0.44 | 25.5639 | 1
2025-11-27 06:21 | 1179151 | 5 | 27 | 1179151 | 27 | 47 | 94 | 20.0629 | 21.8779 | 4912567 | 129 | 3715016 | 102 | 18400 | 0 | 4.302 | 188676 | 0.94 | 100 | 0.59 | 0.48 | 0.44 | 0.43 | 0.46 | 0.44 | 0.44 | 0.43 | 0.43 | 0.42 | 0.6 | 0.45 | 3.985 | 186939 | 0.84 | 100 | 0.56 | 0.4 | 0.39 | 0.35 | 0.42 | 0.45 | 0.42 | 0.45 | 0.41 | 0.41 | 0.57 | 0.43 | 4.03 | 186500 | 0.85 | 100 | 0.51 | 0.43 | 0.42 | 0.44 | 0.4 | 0.44 | 0.42 | 0.44 | 0.45 | 0.42 | 0.55 | 0.44 | 4.932 | 191891 | 1.1 | 100 | 0.66 | 0.56 | 0.53 | 0.51 | 0.53 | 0.49 | 0.52 | 0.53 | 0.54 | 0.52 | 0.65 | 0.58 | 4.691 | 189915 | 1.02 | 100 | 0.64 | 0.53 | 0.5 | 0.5 | 0.51 | 0.51 | 0.53 | 0.51 | 0.48 | 0.49 | 0.65 | 0.5 | 4.691 | 189707 | 1.04 | 100 | 0.64 | 0.5 | 0.47 | 0.46 | 0.47 | 0.46 | 0.46 | 0.49 | 0.5 | 0.45 | 0.63 | 0.46 | 26.553 | 1
2025-11-27 06:22 | 1179152 | 5 | 28 | 1179152 | 28 | 49 | 98 | 20.1194 | 21.8967 | 4912570 | 122 | 3715018 | 94 | 18400 | 0 | 4.473 | 188676 | 1.01 | 100 | 0.61 | 0.5 | 0.47 | 0.45 | 0.49 | 0.46 | 0.46 | 0.45 | 0.45 | 0.45 | 0.62 | 0.47 | 4.181 | 186939 | 0.91 | 100 | 0.59 | 0.42 | 0.42 | 0.39 | 0.44 | 0.44 | 0.42 | 0.46 | 0.42 | 0.43 | 0.59 | 0.44 | 4.244 | 186500 | 0.92 | 100 | 0.54 | 0.47 | 0.45 | 0.43 | 0.43 | 0.48 | 0.45 | 0.45 | 0.46 | 0.45 | 0.56 | 0.47 | 5.136 | 191891 | 1.18 | 100 | 0.68 | 0.58 | 0.59 | 0.57 | 0.59 | 0.53 | 0.54 | 0.55 | 0.57 | 0.53 | 0.67 | 0.6 | 4.602 | 189915 | 1.11 | 100 | 0.67 | 0.55 | 0.23 | 0.54 | 0.53 | 0.52 | 0.52 | 0.52 | 0.5 | 0.49 | 0.68 | 0.51 | 4.917 | 189707 | 1.12 | 100 | 0.66 | 0.53 | 0.53 | 0.48 | 0.51 | 0.51 | 0.47 | 0.51 | 0.54 | 0.49 | 0.67 | 0.49 | 27.5416 | 1
2025-11-27 06:23 | 1179152 | 6 | 29 | 1179152 | 29 | 51 | 102 | 20.1946 | 21.9343 | 4912571 | 129 | 3715019 | 100 | 18400 | 0 | 4.666 | 188676 | 1.09 | 100 | 0.64 | 0.52 | 0.48 | 0.48 | 0.51 | 0.51 | 0.48 | 0.48 | 0.47 | 0.48 | 0.65 | 0.49 | 4.336 | 186939 | 0.98 | 100 | 0.6 | 0.44 | 0.41 | 0.43 | 0.46 | 0.48 | 0.46 | 0.48 | 0.48 | 0.45 | 0.61 | 0.47 | 4.403 | 186500 | 0.99 | 100 | 0.56 | 0.49 | 0.46 | 0.44 | 0.47 | 0.48 | 0.46 | 0.48 | 0.49 | 0.46 | 0.59 | 0.48 | 5.357 | 191891 | 1.27 | 100 | 0.71 | 0.61 | 0.59 | 0.59 | 0.58 | 0.55 | 0.58 | 0.57 | 0.6 | 0.56 | 0.7 | 0.62 | 5.107 | 189915 | 1.19 | 100 | 0.69 | 0.58 | 0.54 | 0.57 | 0.56 | 0.54 | 0.58 | 0.56 | 0.55 | 0.54 | 0.7 | 0.56 | 5.116 | 189708 | 1.2 | 100 | 0.68 | 0.54 | 0.56 | 0.5 | 0.54 | 0.5 | 0.53 | 0.54 | 0.56 | 0.48 | 0.69 | 0.52 | 28.5325 | 1
2025-11-27 06:24 | 1179153 | 6 | 30 | 1179153 | 31 | 53 | 106 | 20.2604 | 21.9813 | 4912574 | 102 | 3715021 | 72 | 18400 | 0 | 4.877 | 188676 | 1.17 | 100 | 0.65 | 0.55 | 0.51 | 0.51 | 0.53 | 0.51 | 0.49 | 0.49 | 0.51 | 0.47 | 0.67 | 0.51 | 4.578 | 186939 | 1.06 | 100 | 0.63 | 0.46 | 0.47 | 0.46 | 0.48 | 0.51 | 0.48 | 0.5 | 0.47 | 0.47 | 0.64 | 0.49 | 4.573 | 186500 | 1.07 | 100 | 0.58 | 0.5 | 0.48 | 0.47 | 0.45 | 0.5 | 0.49 | 0.5 | 0.52 | 0.48 | 0.61 | 0.5 | 5.576 | 191891 | 1.37 | 100 | 0.75 | 0.64 | 0.6 | 0.61 | 0.62 | 0.58 | 0.6 | 0.61 | 0.61 | 0.58 | 0.72 | 0.64 | 5.314 | 189915 | 1.27 | 100 | 0.72 | 0.6 | 0.57 | 0.59 | 0.56 | 0.56 | 0.6 | 0.58 | 0.53 | 0.56 | 0.72 | 0.58 | 5.325 | 189708 | 1.29 | 100 | 0.71 | 0.58 | 0.58 | 0.52 | 0.56 | 0.55 | 0.55 | 0.56 | 0.58 | 0.53 | 0.71 | 0.53 | 29.5229 | 1
2025-11-27 06:25 | 1179153 | 6 | 32 | 1179153 | 32 | 55 | 110 | 20.3451 | 22.0001 | 4912575 | 107 | 3715022 | 75 | 18400 | 0 | 5.075 | 188676 | 1.26 | 100 | 0.68 | 0.58 | 0.53 | 0.52 | 0.55 | 0.52 | 0.52 | 0.5 | 0.52 | 0.51 | 0.69 | 0.53 | 4.75 | 186939 | 1.13 | 100 | 0.65 | 0.48 | 0.47 | 0.48 | 0.51 | 0.51 | 0.51 | 0.51 | 0.49 | 0.49 | 0.65 | 0.5 | 4.79 | 186500 | 1.15 | 100 | 0.6 | 0.53 | 0.51 | 0.53 | 0.52 | 0.52 | 0.51 | 0.53 | 0.54 | 0.52 | 0.63 | 0.53 | 5.767 | 191891 | 1.46 | 100 | 0.76 | 0.65 | 0.63 | 0.61 | 0.65 | 0.59 | 0.62 | 0.62 | 0.65 | 0.6 | 0.75 | 0.67 | 5.526 | 189915 | 1.36 | 100 | 0.74 | 0.62 | 0.59 | 0.61 | 0.6 | 0.58 | 0.62 | 0.59 | 0.56 | 0.57 | 0.75 | 0.59 | 5.529 | 189708 | 1.38 | 100 | 0.73 | 0.61 | 0.6 | 0.55 | 0.58 | 0.57 | 0.58 | 0.59 | 0.59 | 0.56 | 0.74 | 0.57 | 31.5 | 1
2025-11-27 06:26 | 1179154 | 7 | 33 | 1179154 | 33 | 57 | 114 | 20.4297 | 22.0378 | 4912577 | 111 | 3715023 | 78 | 18400 | 0 | 5.246 | 188676 | 1.34 | 100 | 0.71 | 0.6 | 0.58 | 0.55 | 0.57 | 0.54 | 0.54 | 0.54 | 0.56 | 0.53 | 0.72 | 0.55 | 4.897 | 186939 | 1.21 | 100 | 0.67 | 0.5 | 0.5 | 0.5 | 0.53 | 0.55 | 0.49 | 0.52 | 0.51 | 0.52 | 0.68 | 0.53 | 4.966 | 186500 | 1.23 | 100 | 0.63 | 0.55 | 0.53 | 0.51 | 0.53 | 0.54 | 0.53 | 0.55 | 0.56 | 0.53 | 0.65 | 0.55 | 5.999 | 191892 | 1.56 | 100 | 0.79 | 0.68 | 0.66 | 0.64 | 0.68 | 0.62 | 0.65 | 0.65 | 0.67 | 0.63 | 0.78 | 0.7 | 5.755 | 189916 | 1.46 | 100 | 0.77 | 0.65 | 0.62 | 0.63 | 0.63 | 0.6 | 0.64 | 0.62 | 0.58 | 0.61 | 0.78 | 0.62 | 5.746 | 189708 | 1.48 | 100 | 0.75 | 0.63 | 0.63 | 0.57 | 0.61 | 0.6 | 0.61 | 0.62 | 0.62 | 0.59 | 0.75 | 0.58 | 32.4936 | 1
2025-11-27 06:27 | 1179154 | 8 | 34 | 1179154 | 34 | 60 | 120 | 20.4955 | 22.0472 | 4912579 | 169 | 3715025 | 135 | 18400 | 0 | 5.444 | 188677 | 1.43 | 100 | 0.73 | 0.63 | 0.61 | 0.57 | 0.6 | 0.58 | 0.58 | 0.56 | 0.57 | 0.56 | 0.74 | 0.58 | 5.096 | 186939 | 1.3 | 100 | 0.7 | 0.53 | 0.52 | 0.52 | 0.55 | 0.57 | 0.52 | 0.54 | 0.55 | 0.54 | 0.7 | 0.55 | 5.151 | 186500 | 1.31 | 100 | 0.64 | 0.57 | 0.55 | 0.56 | 0.54 | 0.55 | 0.56 | 0.57 | 0.58 | 0.55 | 0.68 | 0.57 | 6.207 | 191892 | 1.66 | 100 | 0.81 | 0.71 | 0.71 | 0.7 | 0.7 | 0.67 | 0.68 | 0.67 | 0.68 | 0.66 | 0.8 | 0.72 | 5.946 | 189916 | 1.56 | 100 | 0.79 | 0.67 | 0.64 | 0.65 | 0.64 | 0.63 | 0.67 | 0.65 | 0.63 | 0.62 | 0.8 | 0.64 | 5.919 | 189708 | 1.57 | 100 | 0.78 | 0.65 | 0.65 | 0.59 | 0.63 | 0.61 | 0.63 | 0.63 | 0.64 | 0.62 | 0.79 | 0.6 | 33.4856 | 1
2025-11-27 06:28 | 1179155 | 8 | 35 | 1179155 | 35 | 62 | 124 | 20.6084 | 22.0942 | 4912582 | 153 | 3715027 | 118 | 18400 | 0 | 5.648 | 188677 | 1.52 | 100 | 0.75 | 0.64 | 0.63 | 0.59 | 0.62 | 0.6 | 0.6 | 0.58 | 0.6 | 0.58 | 0.76 | 0.6 | 5.23 | 186939 | 1.38 | 100 | 0.72 | 0.55 | 0.43 | 0.53 | 0.57 | 0.56 | 0.55 | 0.58 | 0.57 | 0.56 | 0.73 | 0.57 | 5.336 | 186500 | 1.4 | 100 | 0.67 | 0.59 | 0.6 | 0.58 | 0.57 | 0.61 | 0.57 | 0.59 | 0.59 | 0.56 | 0.7 | 0.59 | 6.421 | 191892 | 1.76 | 100 | 0.84 | 0.73 | 0.72 | 0.71 | 0.73 | 0.7 | 0.69 | 0.71 | 0.71 | 0.66 | 0.83 | 0.74 | 6.159 | 189916 | 1.66 | 100 | 0.81 | 0.69 | 0.66 | 0.69 | 0.67 | 0.64 | 0.69 | 0.66 | 0.66 | 0.65 | 0.83 | 0.67 | 6.14 | 189708 | 1.67 | 100 | 0.81 | 0.67 | 0.67 | 0.6 | 0.65 | 0.63 | 0.66 | 0.66 | 0.66 | 0.64 | 0.81 | 0.62 | 34.4836 | 1
2025-11-27 06:29 | 1179156 | 9 | 37 | 1179156 | 37 | 64 | 128 | 20.6836 | 22.1412 | 4912585 | 156 | 3715029 | 119 | 18400 | 0 | 5.839 | 188677 | 1.62 | 100 | 0.77 | 0.66 | 0.66 | 0.61 | 0.61 | 0.64 | 0.61 | 0.6 | 0.61 | 0.6 | 0.78 | 0.61 | 5.483 | 186939 | 1.47 | 100 | 0.74 | 0.57 | 0.56 | 0.57 | 0.59 | 0.59 | 0.58 | 0.6 | 0.6 | 0.59 | 0.75 | 0.6 | 5.532 | 186500 | 1.49 | 100 | 0.69 | 0.62 | 0.62 | 0.61 | 0.59 | 0.63 | 0.6 | 0.62 | 0.62 | 0.59 | 0.72 | 0.61 | 6.654 | 191892 | 1.88 | 100 | 0.86 | 0.75 | 0.76 | 0.75 | 0.75 | 0.73 | 0.72 | 0.73 | 0.73 | 0.7 | 0.85 | 0.77 | 6.385 | 189916 | 1.76 | 100 | 0.84 | 0.73 | 0.67 | 0.72 | 0.7 | 0.68 | 0.72 | 0.69 | 0.68 | 0.67 | 0.85 | 0.68 | 6.365 | 189708 | 1.78 | 100 | 0.84 | 0.7 | 0.7 | 0.64 | 0.68 | 0.66 | 0.67 | 0.69 | 0.69 | 0.66 | 0.84 | 0.65 | 36.4633 | 1
2025-11-27 06:30 | 1179156 | 10 | 38 | 1179156 | 38 | 66 | 132 | 20.7964 | 22.1882 | 4912587 | 158 | 3715031 | 120 | 18400 | 0 | 6.022 | 188677 | 1.72 | 100 | 0.8 | 0.69 | 0.67 | 0.67 | 0.65 | 0.66 | 0.62 | 0.61 | 0.61 | 0.62 | 0.8 | 0.64 | 5.7 | 186939 | 1.57 | 100 | 0.76 | 0.59 | 0.58 | 0.58 | 0.61 | 0.62 | 0.59 | 0.64 | 0.61 | 0.61 | 0.77 | 0.62 | 5.708 | 186500 | 1.58 | 100 | 0.71 | 0.63 | 0.64 | 0.63 | 0.61 | 0.65 | 0.62 | 0.63 | 0.64 | 0.61 | 0.73 | 0.62 | 6.846 | 191892 | 1.98 | 100 | 0.89 | 0.79 | 0.78 | 0.77 | 0.77 | 0.75 | 0.74 | 0.75 | 0.75 | 0.72 | 0.87 | 0.79 | 6.579 | 189916 | 1.87 | 100 | 0.87 | 0.75 | 0.73 | 0.73 | 0.73 | 0.7 | 0.74 | 0.71 | 0.7 | 0.7 | 0.88 | 0.72 | 6.554 | 189708 | 1.88 | 100 | 0.86 | 0.72 | 0.71 | 0.65 | 0.7 | 0.69 | 0.68 | 0.71 | 0.72 | 0.69 | 0.86 | 0.67 | 37.463 | 1
2025-11-27 06:31 | 1179157 | 10 | 39 | 1179157 | 39 | 68 | 136 | 20.8717 | 22.2352 | 4912590 | 160 | 3715033 | 121 | 18400 | 0 | 6.201 | 188677 | 1.81 | 100 | 0.82 | 0.71 | 0.67 | 0.67 | 0.63 | 0.67 | 0.66 | 0.64 | 0.66 | 0.64 | 0.83 | 0.67 | 5.869 | 186940 | 1.66 | 100 | 0.78 | 0.6 | 0.59 | 0.59 | 0.63 | 0.63 | 0.63 | 0.65 | 0.63 | 0.62 | 0.78 | 0.63 | 5.917 | 186500 | 1.68 | 100 | 0.74 | 0.66 | 0.66 | 0.65 | 0.63 | 0.67 | 0.63 | 0.65 | 0.64 | 0.64 | 0.76 | 0.66 | 7.052 | 191892 | 2.1 | 100 | 0.92 | 0.81 | 0.8 | 0.76 | 0.78 | 0.77 | 0.77 | 0.78 | 0.79 | 0.75 | 0.9 | 0.82 | 6.777 | 189916 | 1.99 | 100 | 0.89 | 0.78 | 0.76 | 0.76 | 0.75 | 0.73 | 0.76 | 0.74 | 0.73 | 0.73 | 0.91 | 0.74 | 6.766 | 189708 | 2 | 100 | 0.87 | 0.74 | 0.73 | 0.68 | 0.73 | 0.72 | 0.72 | 0.73 | 0.74 | 0.71 | 0.88 | 0.7 | 38.4586 | 1
2025-11-27 06:32 | 1179158 | 11 | 41 | 1179158 | 41 | 70 | 140 | 20.9563 | 22.2823 | 4912593 | 160 | 3715035 | 119 | 18400 | 0 | 6.412 | 188677 | 1.91 | 100 | 0.85 | 0.73 | 0.69 | 0.68 | 0.71 | 0.72 | 0.68 | 0.67 | 0.67 | 0.68 | 0.86 | 0.69 | 6.055 | 186940 | 1.75 | 100 | 0.8 | 0.63 | 0.62 | 0.64 | 0.66 | 0.66 | 0.66 | 0.68 | 0.63 | 0.64 | 0.81 | 0.66 | 6.076 | 186501 | 1.78 | 100 | 0.75 | 0.67 | 0.68 | 0.67 | 0.65 | 0.7 | 0.65 | 0.67 | 0.68 | 0.65 | 0.79 | 0.67 | 7.258 | 191892 | 2.22 | 100 | 0.94 | 0.83 | 0.82 | 0.8 | 0.82 | 0.81 | 0.79 | 0.81 | 0.8 | 0.77 | 0.92 | 0.84 | 7.008 | 189916 | 2.09 | 100 | 0.92 | 0.8 | 0.77 | 0.78 | 0.77 | 0.76 | 0.77 | 0.76 | 0.75 | 0.74 | 0.92 | 0.75 | 6.964 | 189708 | 2.11 | 100 | 0.89 | 0.76 | 0.76 | 0.72 | 0.75 | 0.73 | 0.74 | 0.76 | 0.77 | 0.74 | 0.91 | 0.73 | 40.4423 | 1
2025-11-27 06:33 | 1179158 | 12 | 42 | 1179158 | 42 | 72 | 144 | 21.0597 | 22.3293 | 4912594 | 120 | 3715036 | 78 | 18400 | 0 | 6.623 | 188677 | 2.03 | 100 | 0.86 | 0.75 | 0.72 | 0.71 | 0.73 | 0.75 | 0.71 | 0.69 | 0.71 | 0.68 | 0.88 | 0.71 | 6.244 | 186940 | 1.86 | 100 | 0.83 | 0.65 | 0.63 | 0.63 | 0.68 | 0.68 | 0.68 | 0.7 | 0.68 | 0.66 | 0.83 | 0.67 | 6.313 | 186501 | 1.89 | 100 | 0.78 | 0.7 | 0.68 | 0.66 | 0.67 | 0.7 | 0.69 | 0.69 | 0.7 | 0.67 | 0.82 | 0.69 | 7.502 | 191892 | 2.34 | 100 | 0.96 | 0.85 | 0.85 | 0.82 | 0.82 | 0.8 | 0.82 | 0.83 | 0.84 | 0.81 | 0.94 | 0.88 | 7.205 | 189916 | 2.21 | 100 | 0.94 | 0.82 | 0.8 | 0.81 | 0.81 | 0.78 | 0.8 | 0.79 | 0.77 | 0.78 | 0.96 | 0.79 | 7.198 | 189709 | 2.23 | 100 | 0.93 | 0.78 | 0.77 | 0.76 | 0.78 | 0.75 | 0.75 | 0.77 | 0.79 | 0.77 | 0.94 | 0.75 | 41.4432 | 1
2025-11-27 06:34 | 1179159 | 12 | 43 | 1179159 | 43 | 74 | 148 | 21.1444 | 22.3763 | 4912597 | 132 | 3715038 | 89 | 18400 | 0 | 6.829 | 188677 | 2.15 | 100 | 0.9 | 0.78 | 0.74 | 0.72 | 0.75 | 0.75 | 0.73 | 0.71 | 0.72 | 0.73 | 0.9 | 0.74 | 6.231 | 186940 | 1.96 | 100 | 0.84 | 0.67 | 0.39 | 0.67 | 0.69 | 0.7 | 0.68 | 0.71 | 0.69 | 0.69 | 0.86 | 0.69 | 6.488 | 186501 | 1.99 | 100 | 0.8 | 0.72 | 0.72 | 0.72 | 0.7 | 0.74 | 0.7 | 0.72 | 0.72 | 0.7 | 0.84 | 0.72 | 7.692 | 191892 | 2.46 | 100 | 0.99 | 0.89 | 0.86 | 0.82 | 0.85 | 0.84 | 0.85 | 0.85 | 0.85 | 0.83 | 0.98 | 0.9 | 7.408 | 189916 | 2.33 | 100 | 0.97 | 0.85 | 0.83 | 0.83 | 0.83 | 0.8 | 0.82 | 0.81 | 0.8 | 0.79 | 0.96 | 0.79 | 7.409 | 189709 | 2.35 | 100 | 0.95 | 0.81 | 0.8 | 0.78 | 0.81 | 0.78 | 0.79 | 0.8 | 0.82 | 0.78 | 0.95 | 0.77 | 42.442 | 1
2025-11-27 06:35 | 1179160 | 13 | 44 | 1179160 | 44 | 76 | 152 | 21.2478 | 22.4233 | 4912599 | 125 | 3715039 | 81 | 18400 | 0 | 7.019 | 188677 | 2.26 | 100 | 0.92 | 0.81 | 0.77 | 0.74 | 0.78 | 0.78 | 0.75 | 0.73 | 0.76 | 0.74 | 0.93 | 0.77 | 6.617 | 186940 | 2.08 | 100 | 0.87 | 0.69 | 0.72 | 0.69 | 0.7 | 0.73 | 0.71 | 0.73 | 0.71 | 0.71 | 0.88 | 0.73 | 6.648 | 186501 | 2.1 | 100 | 0.82 | 0.73 | 0.75 | 0.71 | 0.71 | 0.75 | 0.72 | 0.73 | 0.73 | 0.71 | 0.86 | 0.74 | 7.903 | 191893 | 2.6 | 100 | 1.02 | 0.91 | 0.88 | 0.86 | 0.88 | 0.83 | 0.88 | 0.86 | 0.88 | 0.85 | 1 | 0.92 | 7.618 | 189917 | 2.45 | 100 | 0.99 | 0.88 | 0.85 | 0.83 | 0.84 | 0.83 | 0.85 | 0.84 | 0.82 | 0.82 | 1.01 | 0.83 | 7.584 | 189709 | 2.47 | 100 | 0.97 | 0.83 | 0.82 | 0.77 | 0.83 | 0.79 | 0.81 | 0.83 | 0.85 | 0.81 | 0.97 | 0.79 | 43.4441 | 1
2025-11-27 06:36 | 1179161 | 14 | 46 | 1179161 | 46 | 79 | 158 | 21.3419 | 22.4609 | 4912601 | 122 | 3715040 | 76 | 18400 | 0 | 7.235 | 188678 | 2.38 | 100 | 0.94 | 0.83 | 0.8 | 0.78 | 0.8 | 0.79 | 0.77 | 0.75 | 0.77 | 0.76 | 0.96 | 0.78 | 6.852 | 186940 | 2.19 | 100 | 0.9 | 0.72 | 0.73 | 0.72 | 0.75 | 0.76 | 0.74 | 0.76 | 0.74 | 0.73 | 0.91 | 0.75 | 6.849 | 186501 | 2.21 | 100 | 0.84 | 0.76 | 0.76 | 0.73 | 0.73 | 0.78 | 0.74 | 0.76 | 0.77 | 0.74 | 0.88 | 0.76 | 8.138 | 191893 | 2.73 | 100 | 1.05 | 0.94 | 0.88 | 0.89 | 0.91 | 0.89 | 0.91 | 0.9 | 0.91 | 0.88 | 1.03 | 0.95 | 7.84 | 189917 | 2.59 | 100 | 1.02 | 0.9 | 0.87 | 0.88 | 0.88 | 0.85 | 0.87 | 0.86 | 0.83 | 0.85 | 1.03 | 0.86 | 7.824 | 189709 | 2.6 | 100 | 0.99 | 0.86 | 0.85 | 0.81 | 0.85 | 0.82 | 0.83 | 0.84 | 0.87 | 0.84 | 1 | 0.82 | 45.4333 | 1
2025-11-27 06:37 | 1179161 | 14 | 47 | 1179161 | 47 | 81 | 162 | 21.4359 | 22.4986 | 4912603 | 109 | 3715042 | 62 | 18400 | 0 | 7.438 | 188678 | 2.49 | 100 | 0.96 | 0.84 | 0.83 | 0.81 | 0.82 | 0.8 | 0.79 | 0.77 | 0.8 | 0.79 | 0.97 | 0.8 | 7.014 | 186940 | 2.3 | 100 | 0.92 | 0.73 | 0.73 | 0.72 | 0.76 | 0.78 | 0.75 | 0.78 | 0.76 | 0.74 | 0.93 | 0.77 | 7.052 | 186501 | 2.33 | 100 | 0.86 | 0.78 | 0.79 | 0.76 | 0.76 | 0.81 | 0.77 | 0.78 | 0.8 | 0.76 | 0.91 | 0.79 | 8.345 | 191893 | 2.87 | 100 | 1.08 | 0.97 | 0.91 | 0.92 | 0.94 | 0.91 | 0.93 | 0.93 | 0.92 | 0.91 | 1.05 | 0.98 | 8.045 | 189917 | 2.72 | 100 | 1.04 | 0.93 | 0.9 | 0.91 | 0.89 | 0.88 | 0.9 | 0.88 | 0.84 | 0.87 | 1.06 | 0.89 | 8.08 | 189709 | 2.74 | 100 | 1.02 | 0.88 | 0.88 | 0.83 | 0.88 | 0.83 | 0.86 | 0.87 | 0.9 | 0.86 | 1.02 | 0.85 | 46.4356 | 1
2025-11-27 06:38 | 1179162 | 15 | 48 | 1179162 | 48 | 83 | 166 | 21.5299 | 22.5456 | 4912604 | 101 | 3715042 | 53 | 18400 | 0 | 7.65 | 188678 | 2.62 | 100 | 0.99 | 0.87 | 0.85 | 0.83 | 0.83 | 0.84 | 0.82 | 0.8 | 0.83 | 0.81 | 1 | 0.83 | 7.226 | 186940 | 2.42 | 100 | 0.93 | 0.76 | 0.77 | 0.75 | 0.79 | 0.79 | 0.78 | 0.81 | 0.78 | 0.77 | 0.96 | 0.8 | 7.229 | 186501 | 2.45 | 100 | 0.89 | 0.8 | 0.8 | 0.77 | 0.78 | 0.81 | 0.79 | 0.81 | 0.81 | 0.77 | 0.93 | 0.81 | 8.589 | 191893 | 3.01 | 100 | 1.09 | 0.99 | 0.95 | 0.95 | 0.97 | 0.95 | 0.96 | 0.96 | 0.96 | 0.93 | 1.08 | 1 | 8.302 | 189917 | 2.86 | 100 | 1.07 | 0.95 | 0.93 | 0.93 | 0.92 | 0.9 | 0.92 | 0.9 | 0.88 | 0.89 | 1.08 | 0.9 | 8.294 | 189709 | 2.88 | 100 | 1.05 | 0.91 | 0.91 | 0.86 | 0.9 | 0.86 | 0.89 | 0.91 | 0.92 | 0.87 | 1.03 | 0.86 | 47.4387 | 1
2025-11-27 06:39 | 1179163 | 16 | 50 | 1179163 | 50 | 86 | 172 | 21.6146 | 22.5644 | 4912606 | 94 | 3715043 | 44 | 18400 | 0 | 7.849 | 188678 | 2.75 | 100 | 1.01 | 0.9 | 0.86 | 0.85 | 0.86 | 0.86 | 0.82 | 0.83 | 0.84 | 0.84 | 1.03 | 0.86 | 7.437 | 186940 | 2.54 | 100 | 0.95 | 0.76 | 0.8 | 0.78 | 0.8 | 0.82 | 0.81 | 0.82 | 0.81 | 0.8 | 0.96 | 0.81 | 7.423 | 186501 | 2.56 | 100 | 0.91 | 0.82 | 0.82 | 0.8 | 0.8 | 0.83 | 0.81 | 0.82 | 0.84 | 0.81 | 0.96 | 0.84 | 8.82 | 191893 | 3.15 | 100 | 1.12 | 1.01 | 0.98 | 0.97 | 0.99 | 0.97 | 0.98 | 0.98 | 0.99 | 0.96 | 1.12 | 1.03 | 8.516 | 189917 | 2.99 | 100 | 1.07 | 0.95 | 0.95 | 0.96 | 0.96 | 0.93 | 0.94 | 0.93 | 0.9 | 0.92 | 1.11 | 0.94 | 8.487 | 189709 | 3.01 | 100 | 1.07 | 0.93 | 0.93 | 0.87 | 0.92 | 0.89 | 0.92 | 0.93 | 0.96 | 0.91 | 1.07 | 0.9 | 49.4294 | 1
2025-11-27 06:40 | 1179164 | 16 | 51 | 1179164 | 51 | 88 | 176 | 21.718 | 22.602 | 4912608 | 100 | 3715044 | 49 | 18400 | 0 | 8.053 | 188678 | 2.88 | 100 | 1.04 | 0.93 | 0.9 | 0.89 | 0.89 | 0.89 | 0.86 | 0.85 | 0.87 | 0.86 | 1.06 | 0.88 | 7.625 | 186941 | 2.67 | 100 | 0.99 | 0.79 | 0.81 | 0.79 | 0.83 | 0.84 | 0.81 | 0.85 | 0.84 | 0.81 | 1 | 0.84 | 7.651 | 186501 | 2.69 | 100 | 0.93 | 0.86 | 0.84 | 0.82 | 0.83 | 0.86 | 0.84 | 0.85 | 0.87 | 0.84 | 0.95 | 0.85 | 9.066 | 191893 | 3.3 | 100 | 1.16 | 1.05 | 1 | 1 | 1.01 | 1 | 1.01 | 1.02 | 1.01 | 0.98 | 1.14 | 1.07 | 8.773 | 189917 | 3.14 | 100 | 1.12 | 1.01 | 0.97 | 1 | 0.99 | 0.96 | 0.98 | 0.96 | 0.92 | 0.96 | 1.14 | 0.97 | 8.764 | 189710 | 3.15 | 100 | 1.1 | 0.97 | 0.96 | 0.91 | 0.95 | 0.9 | 0.95 | 0.96 | 0.98 | 0.94 | 1.1 | 0.92 | 50.4355 | 1
2025-11-27 06:41 | 1179165 | 18 | 53 | 1179165 | 53 | 91 | 182 | 21.8121 | 22.6772 | 4912610 | 101 | 3715045 | 48 | 18400 | 0 | 8.27 | 188678 | 3.02 | 100 | 1.07 | 0.96 | 0.91 | 0.91 | 0.91 | 0.89 | 0.9 | 0.88 | 0.9 | 0.89 | 1.08 | 0.91 | 7.851 | 186941 | 2.8 | 100 | 1.01 | 0.82 | 0.81 | 0.82 | 0.86 | 0.87 | 0.84 | 0.88 | 0.86 | 0.84 | 1.03 | 0.87 | 7.86 | 186502 | 2.82 | 100 | 0.96 | 0.88 | 0.87 | 0.85 | 0.85 | 0.87 | 0.86 | 0.86 | 0.89 | 0.86 | 0.99 | 0.88 | 9.34 | 191893 | 3.46 | 100 | 1.18 | 1.09 | 1.02 | 1.04 | 1.05 | 1.04 | 1.04 | 1.04 | 1.04 | 1.02 | 1.18 | 1.09 | 9.049 | 189917 | 3.29 | 100 | 1.16 | 1.06 | 1 | 1.02 | 1.02 | 1 | 1.01 | 1 | 0.96 | 0.98 | 1.18 | 1 | 9.014 | 189710 | 3.31 | 100 | 1.11 | 0.97 | 0.99 | 0.94 | 0.97 | 0.93 | 0.98 | 0.99 | 1.01 | 0.98 | 1.14 | 0.95 | 52.43 | 1
2025-11-27 06:42 | 1179166 | 19 | 54 | 1179166 | 54 | 94 | 188 | 21.9343 | 22.696 | 4912612 | 102 | 3715046 | 48 | 18400 | 0 | 8.54 | 188678 | 3.16 | 100 | 1.09 | 0.98 | 0.94 | 0.93 | 0.95 | 0.92 | 0.92 | 0.9 | 0.93 | 0.92 | 1.11 | 0.93 | 8.091 | 186941 | 2.93 | 100 | 1.03 | 0.84 | 0.85 | 0.84 | 0.88 | 0.88 | 0.86 | 0.89 | 0.89 | 0.87 | 1.05 | 0.89 | 8.037 | 186502 | 2.95 | 100 | 0.99 | 0.91 | 0.88 | 0.86 | 0.85 | 0.88 | 0.89 | 0.89 | 0.92 | 0.89 | 1.03 | 0.92 | 9.613 | 191894 | 3.62 | 100 | 1.21 | 1.11 | 1.07 | 1.07 | 1.08 | 1.06 | 1.07 | 1.08 | 1.09 | 1.05 | 1.21 | 1.13 | 9.288 | 189918 | 3.43 | 100 | 1.18 | 1.06 | 1.02 | 1.05 | 1.04 | 1.03 | 1.04 | 1.02 | 1 | 1.01 | 1.21 | 1.03 | 9.274 | 189710 | 3.45 | 100 | 1.16 | 1.02 | 1.01 | 0.97 | 1.02 | 0.97 | 1.01 | 1.02 | 1.05 | 1 | 1.17 | 0.98 | 53.4413 | 1
2025-11-27 06:43 | 1179167 | 19 | 56 | 1179167 | 56 | 97 | 194 | 22.0284 | 22.7431 | 4912614 | 103 | 3715047 | 47 | 18400 | 0 | 8.762 | 188678 | 3.3 | 100 | 1.13 | 1.01 | 0.98 | 0.97 | 0.98 | 0.93 | 0.95 | 0.94 | 0.96 | 0.94 | 1.15 | 0.96 | 8.321 | 186941 | 3.06 | 100 | 1.07 | 0.87 | 0.88 | 0.87 | 0.91 | 0.91 | 0.89 | 0.92 | 0.9 | 0.9 | 1.09 | 0.92 | 8.33 | 186502 | 3.09 | 100 | 1.01 | 0.93 | 0.92 | 0.89 | 0.91 | 0.9 | 0.92 | 0.91 | 0.94 | 0.9 | 1.04 | 0.93 | 9.908 | 191894 | 3.78 | 100 | 1.24 | 1.15 | 1.1 | 1.11 | 1.12 | 1.1 | 1.11 | 1.12 | 1.12 | 1.09 | 1.24 | 1.16 | 9.597 | 189918 | 3.6 | 100 | 1.22 | 1.11 | 1.07 | 1.08 | 1.08 | 1.05 | 1.07 | 1.04 | 1.02 | 1.03 | 1.23 | 1.07 | 9.582 | 189710 | 3.6 | 100 | 1.18 | 1.05 | 1.05 | 1.01 | 1.05 | 1 | 1.04 | 1.06 | 1.08 | 1.04 | 1.2 | 1.01 | 55.4382 | 1
2025-11-27 06:44 | 1179167 | 21 | 58 | 1179167 | 58 | 100 | 200 | 22.1318 | 22.7713 | 4912614 | 103 | 3715047 | 45 | 18400 | 0 | 9.073 | 188679 | 3.45 | 100 | 1.17 | 1.05 | 1.02 | 0.99 | 1.02 | 1 | 0.99 | 0.96 | 1 | 0.98 | 1.18 | 1 | 8.565 | 186941 | 3.2 | 100 | 1.1 | 0.91 | 0.91 | 0.89 | 0.94 | 0.94 | 0.9 | 0.93 | 0.93 | 0.93 | 1.12 | 0.94 | 8.584 | 186502 | 3.24 | 100 | 1.04 | 0.96 | 0.95 | 0.92 | 0.92 | 0.94 | 0.95 | 0.94 | 0.96 | 0.93 | 1.1 | 0.97 | 10.249 | 191894 | 3.94 | 100 | 1.28 | 1.2 | 1.15 | 1.15 | 1.17 | 1.14 | 1.15 | 1.15 | 1.15 | 1.12 | 1.25 | 1.18 | 9.919 | 189918 | 3.76 | 100 | 1.26 | 1.15 | 1.1 | 1.12 | 1.13 | 1.1 | 1.1 | 1.1 | 1.07 | 1.07 | 1.27 | 1.1 | 9.886 | 189710 | 3.77 | 100 | 1.23 | 1.1 | 1.09 | 1.01 | 1.09 | 1.04 | 1.07 | 1.08 | 1.12 | 1.05 | 1.22 | 1.04 | 57.4382 | 1
2025-11-27 06:45 | 1179168 | 21 | 60 | 1179168 | 60 | 103 | 206 | 22.2258 | 22.8371 | 4912616 | 103 | 3715048 | 43 | 18400 | 0 | 9.33 | 188679 | 3.61 | 100 | 1.2 | 1.09 | 1.05 | 1.02 | 1.05 | 1.03 | 1.02 | 0.98 | 1.03 | 1.01 | 1.21 | 1.03 | 8.862 | 186941 | 3.36 | 100 | 1.13 | 0.94 | 0.94 | 0.92 | 0.96 | 0.96 | 0.95 | 0.98 | 0.96 | 0.95 | 1.15 | 0.98 | 8.836 | 186502 | 3.37 | 100 | 1.07 | 0.99 | 0.98 | 0.95 | 0.96 | 0.98 | 0.97 | 0.96 | 1 | 0.96 | 1.11 | 1 | 10.586 | 191894 | 4.12 | 100 | 1.33 | 1.24 | 1.18 | 1.18 | 1.21 | 1.18 | 1.2 | 1.2 | 1.2 | 1.16 | 1.3 | 1.23 | 10.252 | 189918 | 3.93 | 100 | 1.29 | 1.19 | 1.15 | 1.15 | 1.17 | 1.14 | 1.14 | 1.14 | 1.1 | 1.09 | 1.32 | 1.14 | 10.213 | 189710 | 3.93 | 100 | 1.26 | 1.13 | 1.12 | 1.07 | 1.13 | 1.07 | 1.11 | 1.13 | 1.13 | 1.11 | 1.25 | 1.07 | 59.4377 | 1
2025-11-27 06:46 | 1179169 | 21 | 62 | 1179169 | 62 | 107 | 214 | 22.3481 | 22.9123 | 4912618 | 99 | 3715049 | 37 | 18400 | 0 | 9.659 | 188679 | 3.77 | 100 | 1.24 | 1.12 | 1.08 | 1.07 | 1.09 | 1.08 | 1.05 | 1.02 | 1.06 | 1.05 | 1.24 | 1.05 | 9.086 | 186941 | 3.49 | 100 | 1.15 | 0.96 | 0.96 | 0.94 | 0.99 | 1 | 0.98 | 1.01 | 0.99 | 0.99 | 1.18 | 1.01 | 9.1 | 186502 | 3.52 | 100 | 1.1 | 1.02 | 1.01 | 0.98 | 0.99 | 0.99 | 1 | 1.01 | 1.03 | 0.99 | 1.16 | 1.04 | 10.971 | 191894 | 4.3 | 100 | 1.37 | 1.27 | 1.22 | 1.22 | 1.24 | 1.22 | 1.24 | 1.23 | 1.24 | 1.21 | 1.35 | 1.28 | 10.626 | 189918 | 4.1 | 100 | 1.34 | 1.23 | 1.2 | 1.2 | 1.21 | 1.17 | 1.19 | 1.19 | 1.15 | 1.15 | 1.36 | 1.17 | 10.596 | 189710 | 4.11 | 100 | 1.31 | 1.17 | 1.17 | 1.11 | 1.16 | 1.12 | 1.16 | 1.17 | 1.17 | 1.15 | 1.29 | 1.11 | 61.4444 | 1
2025-11-27 06:47 | 1179170 | 23 | 64 | 1179171 | 64 | 110 | 220 | 22.4421 | 22.9405 | 4912620 | 123 | 3715050 | 59 | 18400 | 0 | 9.928 | 188679 | 3.93 | 100 | 1.27 | 1.16 | 1.1 | 1.11 | 1.12 | 1.1 | 1.08 | 1.06 | 1.09 | 1.09 | 1.26 | 1.08 | 9.356 | 186942 | 3.66 | 100 | 1.18 | 1 | 1 | 0.98 | 1.01 | 1.04 | 1 | 1.04 | 1.03 | 1.02 | 1.23 | 1.06 | 9.339 | 186502 | 3.68 | 100 | 1.12 | 1.04 | 1.03 | 1.01 | 1.02 | 1.04 | 1.02 | 1.03 | 1.06 | 1.03 | 1.2 | 1.08 | 11.334 | 191894 | 4.48 | 100 | 1.41 | 1.31 | 1.27 | 1.27 | 1.26 | 1.26 | 1.29 | 1.28 | 1.28 | 1.27 | 1.38 | 1.32 | 10.979 | 189918 | 4.27 | 100 | 1.38 | 1.28 | 1.24 | 1.25 | 1.24 | 1.22 | 1.24 | 1.22 | 1.19 | 1.2 | 1.4 | 1.21 | 10.958 | 189711 | 4.29 | 100 | 1.35 | 1.23 | 1.22 | 1.16 | 1.22 | 1.16 | 1.2 | 1.21 | 1.24 | 1.2 | 1.35 | 1.17 | 63.4466 | 1
2025-11-27 06:48 | 1179172 | 24 | 66 | 1179172 | 66 | 114 | 228 | 22.5456 | 23.0064 | 4912623 | 120 | 3715051 | 54 | 18400 | 0 | 10.228 | 188679 | 4.08 | 100 | 1.31 | 1.19 | 1.16 | 1.14 | 1.16 | 1.14 | 1.13 | 1.1 | 1.14 | 1.08 | 1.3 | 1.13 | 9.605 | 186942 | 3.8 | 100 | 1.19 | 1 | 1.03 | 1.01 | 1.05 | 1.06 | 1.04 | 1.08 | 1.06 | 1.05 | 1.25 | 1.08 | 9.644 | 186503 | 3.83 | 100 | 1.16 | 1.09 | 1.05 | 1.04 | 1.05 | 1.08 | 1.07 | 1.06 | 1.09 | 1.06 | 1.22 | 1.11 | 11.76 | 191895 | 4.66 | 100 | 1.45 | 1.37 | 1.32 | 1.32 | 1.33 | 1.31 | 1.33 | 1.33 | 1.34 | 1.3 | 1.44 | 1.38 | 11.386 | 189919 | 4.46 | 100 | 1.43 | 1.32 | 1.29 | 1.3 | 1.29 | 1.28 | 1.28 | 1.25 | 1.24 | 1.25 | 1.46 | 1.27 | 11.37 | 189711 | 4.47 | 100 | 1.4 | 1.28 | 1.26 | 1.19 | 1.25 | 1.2 | 1.25 | 1.26 | 1.29 | 1.25 | 1.4 | 1.21 | 65.4522 | 1
2025-11-27 06:49 | 1179173 | 24 | 68 | 1179173 | 69 | 119 | 238 | 22.6584 | 23.0346 | 4912624 | 117 | 3715051 | 49 | 18400 | 0 | 10.599 | 188679 | 4.27 | 100 | 1.35 | 1.24 | 1.2 | 1.18 | 1.21 | 1.19 | 1.16 | 1.14 | 1.18 | 1.14 | 1.35 | 1.17 | 9.902 | 186942 | 3.97 | 100 | 1.25 | 1.05 | 1.05 | 1.04 | 1.07 | 1.09 | 1.07 | 1.09 | 1.09 | 1.07 | 1.29 | 1.11 | 9.902 | 186503 | 4 | 100 | 1.18 | 1.11 | 1.1 | 1.08 | 1.08 | 1.1 | 1.1 | 1.08 | 1.13 | 1.1 | 1.25 | 1.15 | 12.223 | 191895 | 4.87 | 100 | 1.51 | 1.41 | 1.36 | 1.37 | 1.39 | 1.35 | 1.39 | 1.37 | 1.36 | 1.35 | 1.51 | 1.43 | 11.835 | 189919 | 4.66 | 100 | 1.48 | 1.38 | 1.34 | 1.35 | 1.33 | 1.33 | 1.33 | 1.3 | 1.29 | 1.3 | 1.51 | 1.33 | 11.82 | 189711 | 4.67 | 100 | 1.45 | 1.31 | 1.31 | 1.24 | 1.28 | 1.25 | 1.3 | 1.31 | 1.32 | 1.3 | 1.44 | 1.25 | 67.4613 | 1
2025-11-27 06:50 | 1179174 | 27 | 71 | 1179174 | 71 | 123 | 246 | 22.7713 | 23.1004 | 4912626 | 115 | 3715052 | 44 | 18400 | 0 | 10.884 | 188680 | 4.44 | 100 | 1.38 | 1.27 | 1.23 | 1.21 | 1.24 | 1.23 | 1.19 | 1.17 | 1.21 | 1.17 | 1.39 | 1.21 | 10.17 | 186942 | 4.14 | 100 | 1.27 | 1.08 | 1.09 | 1.06 | 1.12 | 1.11 | 1.11 | 1.13 | 1.1 | 1.11 | 1.31 | 1.14 | 10.215 | 186503 | 4.17 | 100 | 1.22 | 1.15 | 1.12 | 1.1 | 1.11 | 1.12 | 1.13 | 1.12 | 1.15 | 1.13 | 1.3 | 1.19 | 12.732 | 191895 | 5.08 | 100 | 1.57 | 1.48 | 1.42 | 1.43 | 1.44 | 1.41 | 1.44 | 1.43 | 1.43 | 1.39 | 1.57 | 1.5 | 12.34 | 189919 | 4.86 | 100 | 1.53 | 1.43 | 1.39 | 1.4 | 1.41 | 1.39 | 1.4 | 1.38 | 1.34 | 1.35 | 1.57 | 1.39 | 12.339 | 189711 | 4.87 | 100 | 1.5 | 1.37 | 1.36 | 1.3 | 1.36 | 1.27 | 1.36 | 1.34 | 1.39 | 1.35 | 1.5 | 1.31 | 70.4645 | 1
2025-11-27 06:51 | 1179175 | 28 | 74 | 1179175 | 74 | 131 | 262 | 22.8935 | 23.1286 | 4912628 | 109 | 3715053 | 35 | 18400 | 0 | 11.357 | 188680 | 4.64 | 100 | 1.44 | 1.33 | 1.3 | 1.26 | 1.29 | 1.27 | 1.24 | 1.23 | 1.27 | 1.21 | 1.44 | 1.26 | 10.535 | 186942 | 4.31 | 100 | 1.27 | 1.09 | 1.11 | 1.1 | 1.14 | 1.15 | 1.13 | 1.16 | 1.14 | 1.13 | 1.37 | 1.2 | 10.55 | 186503 | 4.34 | 100 | 1.24 | 1.18 | 1.16 | 1.12 | 1.15 | 1.14 | 1.15 | 1.16 | 1.18 | 1.16 | 1.35 | 1.25 | 13.479 | 191895 | 5.28 | 100 | 1.55 | 1.45 | 1.5 | 1.51 | 1.53 | 1.51 | 1.52 | 1.51 | 1.52 | 1.49 | 1.56 | 1.5 | 12.999 | 189919 | 5.05 | 100 | 1.54 | 1.44 | 1.47 | 1.5 | 1.5 | 1.47 | 1.48 | 1.45 | 1.43 | 1.44 | 1.6 | 1.42 | 12.999 | 189711 | 5.05 | 100 | 1.52 | 1.38 | 1.45 | 1.37 | 1.45 | 1.38 | 1.44 | 1.42 | 1.49 | 1.44 | 1.53 | 1.34 | 73.4722 | 1
2025-11-27 06:52 | 1179176 | 28 | 81 | 1179176 | 81 | 145 | 290 | 23.0158 | 23.2227 | 4912630 | 171 | 3715054 | 90 | 18400 | 0 | 12.014 | 188680 | 4.82 | 100 | 1.51 | 1.41 | 1.38 | 1.34 | 1.38 | 1.37 | 1.32 | 1.3 | 1.35 | 1.25 | 1.53 | 1.35 | 10.905 | 186942 | 4.49 | 100 | 1.34 | 1.14 | 1.15 | 1.14 | 1.18 | 1.19 | 1.15 | 1.2 | 1.17 | 1.17 | 1.44 | 1.28 | 10.932 | 186503 | 4.52 | 100 | 1.26 | 1.19 | 1.2 | 1.17 | 1.18 | 1.19 | 1.19 | 1.18 | 1.22 | 1.18 | 1.44 | 1.34 | 15.107 | 191895 | 5.5 | 100 | 1.83 | 1.74 | 1.69 | 1.68 | 1.7 | 1.7 | 1.66 | 1.69 | 1.7 | 1.68 | 1.85 | 1.79 | 14.708 | 189919 | 5.28 | 100 | 1.76 | 1.7 | 1.65 | 1.68 | 1.67 | 1.65 | 1.66 | 1.64 | 1.62 | 1.61 | 1.83 | 1.66 | 14.677 | 189712 | 5.28 | 100 | 1.75 | 1.61 | 1.63 | 1.52 | 1.6 | 1.56 | 1.61 | 1.61 | 1.66 | 1.61 | 1.76 | 1.57 | 80.4556 | 1
2025-11-27 06:53 | 1179178 | 30 | 91 | 1179178 | 91 | 167 | 334 | 23.1474 | 23.2509 | 4912633 | 147 | 3715055 | 56 | 18400 | 0 | 12.926 | 188680 | 5.03 | 100 | 1.63 | 1.53 | 1.48 | 1.46 | 1.49 | 1.47 | 1.44 | 1.41 | 1.47 | 1.28 | 1.63 | 1.45 | 11.34 | 186943 | 4.68 | 100 | 1.36 | 1.16 | 1.16 | 1.17 | 1.2 | 1.21 | 1.19 | 1.23 | 1.2 | 1.2 | 1.57 | 1.41 | 11.425 | 186503 | 4.71 | 100 | 1.3 | 1.24 | 1.21 | 1.17 | 1.21 | 1.22 | 1.22 | 1.22 | 1.26 | 1.23 | 1.57 | 1.47 | 17.62 | 191896 | 5.79 | 100 | 2.12 | 2.04 | 1.98 | 1.96 | 2 | 1.98 | 1.81 | 1.97 | 1.97 | 1.96 | 2.15 | 2.08 | 16.983 | 189920 | 5.52 | 100 | 2.02 | 1.98 | 1.9 | 1.96 | 1.95 | 1.91 | 1.93 | 1.9 | 1.9 | 1.86 | 2.13 | 1.94 | 17.018 | 189712 | 5.54 | 100 | 2.01 | 1.87 | 1.89 | 1.79 | 1.88 | 1.8 | 1.87 | 1.83 | 1.94 | 1.87 | 2.04 | 1.83 | 90.4287 | 1
2025-11-27 06:54 | 1179179 | 32 | 98 | 1179179 | 98 | 192 | 384 | 23.2979 | 23.3167 | 4912635 | 147 | 3715056 | 49 | 18400 | 0 | 13.88 | 188680 | 5.25 | 100 | 1.75 | 1.64 | 1.6 | 1.58 | 1.6 | 1.6 | 1.57 | 1.54 | 1.59 | 1.31 | 1.74 | 1.55 | 11.738 | 186943 | 4.86 | 100 | 1.4 | 1.19 | 1.2 | 1.18 | 1.22 | 1.25 | 1.22 | 1.25 | 1.23 | 1.23 | 1.69 | 1.54 | 11.837 | 186504 | 4.89 | 100 | 1.34 | 1.29 | 1.24 | 1.22 | 1.24 | 1.25 | 1.23 | 1.25 | 1.27 | 1.28 | 1.7 | 1.61 | 19.494 | 191896 | 6.09 | 100 | 2.1 | 1.99 | 2.23 | 2.22 | 2.29 | 2.3 | 2.21 | 2.32 | 2.27 | 2.26 | 2.07 | 2.08 | 19.514 | 189920 | 5.85 | 100 | 2.24 | 2.21 | 2.22 | 2.27 | 2.27 | 2.22 | 2.23 | 2.21 | 2.2 | 2.18 | 2.38 | 2.18 | 19.025 | 189712 | 5.87 | 100 | 2 | 1.85 | 2.17 | 2.08 | 2.22 | 2.1 | 2.18 | 2.17 | 2.23 | 2.17 | 2.07 | 1.87 | 97.4345 | 1
2025-11-27 06:55 | 1179181 | 32 | 103 | 1179181 | 103 | 211 | 422 | 23.4578 | 23.4013 | 4912638 | 152 | 3715057 | 49 | 18400 | 0 | 14.706 | 188681 | 5.49 | 100 | 1.84 | 1.74 | 1.69 | 1.66 | 1.71 | 1.7 | 1.68 | 1.63 | 1.69 | 1.35 | 1.84 | 1.65 | 12.124 | 186943 | 5.07 | 100 | 1.43 | 1.22 | 1.23 | 1.19 | 1.25 | 1.27 | 1.24 | 1.27 | 1.26 | 1.25 | 1.81 | 1.66 | 12.241 | 186504 | 5.1 | 100 | 1.36 | 1.31 | 1.25 | 1.24 | 1.25 | 1.27 | 1.27 | 1.27 | 1.3 | 1.3 | 1.83 | 1.74 | 20.009 | 191896 | 6.43 | 100 | 1.55 | 1.38 | 2.58 | 2.58 | 2.63 | 2.65 | 2.5 | 2.66 | 2.61 | 2.58 | 1.43 | 1.56 | 19.983 | 189920 | 6.19 | 100 | 1.72 | 1.59 | 2.52 | 2.56 | 2.57 | 2.52 | 2.44 | 2.46 | 2.5 | 2.47 | 1.82 | 1.57 | 19.992 | 189713 | 6.18 | 100 | 1.7 | 1.55 | 2.36 | 2.35 | 2.49 | 2.37 | 2.47 | 2.45 | 2.43 | 2.47 | 1.75 | 1.56 | 102.4612 | 1
2025-11-27 06:56 | 1179183 | 35 | 104 | 1179183 | 104 | 219 | 438 | 23.6364 | 23.4766 | 4912641 | 151 | 3715058 | 47 | 18400 | 0 | 15.316 | 188681 | 5.75 | 100 | 1.9 | 1.81 | 1.74 | 1.71 | 1.74 | 1.76 | 1.74 | 1.7 | 1.74 | 1.37 | 1.89 | 1.7 | 12.467 | 186943 | 5.27 | 100 | 1.45 | 1.25 | 1.25 | 1.24 | 1.28 | 1.3 | 1.28 | 1.31 | 1.3 | 1.27 | 1.85 | 1.69 | 12.596 | 186504 | 5.31 | 100 | 1.38 | 1.32 | 1.3 | 1.27 | 1.28 | 1.3 | 1.3 | 1.3 | 1.33 | 1.32 | 1.89 | 1.8 | 20.008 | 191897 | 6.74 | 100 | 1.42 | 1.23 | 2.57 | 2.55 | 2.58 | 2.56 | 2.56 | 2.61 | 2.63 | 2.57 | 1.28 | 1.44 | 19.988 | 189921 | 6.5 | 100 | 1.49 | 1.35 | 2.64 | 2.68 | 2.7 | 2.64 | 2.55 | 2.58 | 2.61 | 2.57 | 1.59 | 1.32 | 20.007 | 189713 | 6.52 | 100 | 1.43 | 1.29 | 2.46 | 2.46 | 2.61 | 2.49 | 2.59 | 2.57 | 2.54 | 2.58 | 1.5 | 1.32 | 103.5187 | 1
2025-11-27 06:57 | 1179185 | 37 | 84 | 1179185 | 88 | 225 | 450 | 23.8245 | 23.5988 | 4912643 | 115 | 3715058 | 31 | 18400 | 0 | 14.22 | 188681 | 5.99 | 100 | 1.26 | 1.14 | 1.75 | 1.75 | 1.77 | 1.8 | 1.76 | 1.74 | 1.76 | 1.35 | 1.35 | 1.11 | 12.64 | 186943 | 5.49 | 100 | 1.47 | 1.25 | 1.26 | 1.24 | 1.29 | 1.31 | 1.29 | 1.32 | 1.3 | 1.29 | 1.92 | 1.77 | 12.754 | 186504 | 5.51 | 100 | 1.4 | 1.35 | 1.3 | 1.27 | 1.3 | 1.29 | 1.29 | 1.32 | 1.34 | 1.34 | 1.95 | 1.85 | 15 | 191897 | 7.07 | 100 | 0.99 | 0.77 | 1.68 | 1.81 | 1.84 | 1.79 | 1.79 | 1.85 | 1.89 | 1.82 | 0.88 | 1.09 | 14 | 189921 | 6.82 | 100 | 0.97 | 0.82 | 1.68 | 1.71 | 1.72 | 1.7 | 1.65 | 1.69 | 1.73 | 1.72 | 1.07 | 0.78 | 14.004 | 189713 | 6.84 | 100 | 0.95 | 0.79 | 1.67 | 1.63 | 1.69 | 1.62 | 1.61 | 1.68 | 1.72 | 1.67 | 1.01 | 0.82 | 83.6646 | 1
2025-11-27 06:58 | 1179186 | 37 | 85 | 1179186 | 85 | 230 | 460 | 24.022 | 23.6835 | 4912645 | 114 | 3715059 | 29 | 18400 | 0 | 13.991 | 188681 | 6.23 | 14 | 1.15 | 1.03 | 1.8 | 1.8 | 1.82 | 1.84 | 1.8 | 1.79 | 1.81 | 1.38 | 1.25 | 1 | 12.851 | 186944 | 5.69 | 14 | 1.48 | 1.27 | 1.28 | 1.27 | 1.32 | 1.33 | 1.27 | 1.34 | 1.31 | 1.32 | 1.97 | 1.82 | 12.96 | 186505 | 5.73 | 14 | 1.42 | 1.37 | 1.34 | 1.28 | 1.33 | 1.33 | 1.31 | 1.32 | 1.38 | 1.34 | 1.98 | 1.89 | 13.999 | 191897 | 7.31 | 14 | 0.99 | 0.77 | 1.68 | 1.67 | 1.71 | 1.66 | 1.66 | 1.71 | 1.75 | 1.68 | 0.8 | 1.03 | 14.003 | 189921 | 7.07 | 14 | 0.98 | 0.81 | 1.68 | 1.71 | 1.72 | 1.7 | 1.65 | 1.68 | 1.73 | 1.71 | 1.08 | 0.77 | 14.015 | 189713 | 7.07 | 14 | 0.95 | 0.79 | 1.67 | 1.62 | 1.7 | 1.62 | 1.61 | 1.68 | 1.71 | 1.68 | 1.01 | 0.81 | 84.7175 | 7.5295e-06
2025-11-27 06:59 | 1179188 | 40 | 122 | 1179188 | 122 | 235 | 470 | 24.2289 | 23.7399 | 4912648 | 181 | 3715060 | 59 | 18400 | 0 | 16.278 | 188682 | 6.49 | 100 | 2.01 | 1.92 | 1.85 | 1.85 | 1.87 | 1.89 | 1.85 | 1.81 | 1.88 | 1.43 | 2.03 | 1.84 | 13.018 | 186944 | 5.91 | 100 | 1.46 | 1.27 | 1.3 | 1.26 | 1.33 | 1.35 | 1.33 | 1.36 | 1.34 | 1.33 | 2.02 | 1.87 | 13.167 | 186505 | 5.95 | 100 | 1.44 | 1.39 | 1.35 | 1.31 | 1.34 | 1.34 | 1.34 | 1.35 | 1.38 | 1.35 | 2.02 | 1.93 | 25.001 | 191898 | 7.62 | 100 | 2.61 | 2.51 | 2.89 | 2.89 | 2.97 | 2.98 | 2.83 | 2.99 | 2.93 | 2.92 | 2.57 | 2.61 | 24.993 | 189921 | 7.36 | 100 | 2.95 | 2.89 | 2.81 | 2.9 | 2.87 | 2.81 | 2.87 | 2.77 | 2.84 | 2.79 | 2.98 | 2.79 | 25.006 | 189714 | 7.36 | 100 | 2.82 | 2.68 | 2.7 | 2.65 | 2.81 | 2.69 | 2.79 | 2.77 | 2.78 | 2.78 | 2.92 | 2.68 | 121.68 | 1
2025-11-27 07:00 | 1179190 | 42 | 124 | 1179190 | 124 | 235 | 470 | 24.4358 | 23.8997 | 4912651 | 189 | 3715061 | 65 | 18400 | 0 | 16.417 | 188682 | 6.76 | 100 | 2.03 | 1.94 | 1.87 | 1.86 | 1.89 | 1.91 | 1.89 | 1.83 | 1.89 | 1.45 | 2.06 | 1.86 | 13.175 | 186944 | 6.14 | 100 | 1.48 | 1.29 | 1.32 | 1.3 | 1.35 | 1.37 | 1.34 | 1.36 | 1.36 | 1.35 | 2.03 | 1.89 | 13.318 | 186505 | 6.16 | 100 | 1.43 | 1.35 | 1.36 | 1.33 | 1.35 | 1.35 | 1.36 | 1.36 | 1.4 | 1.39 | 2.06 | 1.97 | 25.019 | 191898 | 8.01 | 100 | 2.6 | 2.5 | 2.88 | 2.89 | 2.97 | 3 | 2.84 | 3.01 | 2.95 | 2.94 | 3.09 | 3.04 | 24.977 | 189922 | 7.77 | 100 | 2.85 | 2.81 | 2.82 | 2.91 | 2.91 | 2.86 | 2.86 | 2.82 | 2.85 | 2.82 | 3.11 | 2.92 | 24.995 | 189714 | 7.77 | 100 | 2.77 | 2.63 | 2.81 | 2.67 | 2.82 | 2.71 | 2.8 | 2.78 | 2.85 | 2.8 | 2.87 | 2.64 | 123.7619 | 1
2025-11-27 07:01 | 1179192 | 42 | 125 | 1179192 | 125 | 237 | 474 | 24.6615 | 24.0126 | 4912654 | 256 | 3715062 | 131 | 18400 | 0 | 16.703 | 188682 | 7.04 | 100 | 2.08 | 1.98 | 1.92 | 1.92 | 1.93 | 1.95 | 1.92 | 1.86 | 1.92 | 1.46 | 2.1 | 1.9 | 13.289 | 186944 | 6.34 | 100 | 1.53 | 1.31 | 1.32 | 1.32 | 1.37 | 1.38 | 1.33 | 1.35 | 1.35 | 1.35 | 2.06 | 1.91 | 13.445 | 186505 | 6.39 | 100 | 1.45 | 1.39 | 1.38 | 1.34 | 1.36 | 1.36 | 1.37 | 1.38 | 1.42 | 1.4 | 2.06 | 1.98 | 26.317 | 191898 | 8.47 | 100 | 3.05 | 2.98 | 2.95 | 2.95 | 3.03 | 3.02 | 3.04 | 2.95 | 2.94 | 2.95 | 3.09 | 3.07 | 25.514 | 189922 | 8.19 | 100 | 3.04 | 3 | 2.87 | 2.94 | 2.94 | 2.89 | 2.91 | 2.85 | 2.88 | 2.8 | 3.15 | 2.95 | 25.42 | 189715 | 8.24 | 100 | 2.95 | 2.81 | 2.83 | 2.69 | 2.86 | 2.72 | 2.83 | 2.74 | 2.92 | 2.83 | 3.01 | 2.75 | 124.8559 | 1
2025-11-27 07:02 | 1179194 | 46 | 127 | 1179194 | 127 | 240 | 480 | 24.8683 | 24.1442 | 4912658 | 255 | 3715064 | 128 | 18400 | 0 | 17.013 | 188682 | 7.34 | 100 | 2.11 | 2.03 | 1.96 | 1.95 | 1.95 | 1.98 | 1.95 | 1.92 | 1.98 | 1.44 | 2.12 | 1.93 | 13.462 | 186944 | 6.57 | 100 | 1.55 | 1.34 | 1.34 | 1.33 | 1.38 | 1.4 | 1.35 | 1.38 | 1.39 | 1.37 | 2.06 | 1.9 | 13.658 | 186505 | 6.62 | 100 | 1.46 | 1.4 | 1.4 | 1.35 | 1.38 | 1.39 | 1.39 | 1.39 | 1.43 | 1.44 | 2.1 | 2.01 | 26.737 | 191899 | 8.91 | 100 | 3.13 | 3.07 | 3.02 | 3 | 3.08 | 3.07 | 3.08 | 3.02 | 3.01 | 3 | 3.22 | 3.18 | 25.838 | 189923 | 8.64 | 100 | 3.1 | 3.05 | 2.92 | 2.97 | 2.97 | 2.91 | 2.92 | 2.88 | 2.92 | 2.85 | 3.2 | 2.99 | 25.7 | 189715 | 8.62 | 100 | 3 | 2.86 | 2.82 | 2.69 | 2.91 | 2.76 | 2.84 | 2.82 | 2.94 | 2.88 | 2.99 | 2.77 | 126.943 | 1
2025-11-27 07:03 | 1179196 | 48 | 129 | 1179196 | 129 | 244 | 488 | 25.0846 | 24.2477 | 4912663 | 255 | 3715067 | 126 | 18400 | 0 | 17.262 | 188683 | 7.6 | 100 | 2.14 | 2.05 | 1.99 | 1.96 | 1.97 | 2.01 | 1.96 | 1.95 | 1.99 | 1.49 | 2.16 | 1.96 | 13.652 | 186945 | 6.8 | 100 | 1.54 | 1.34 | 1.3 | 1.34 | 1.38 | 1.37 | 1.38 | 1.41 | 1.39 | 1.38 | 2.12 | 1.98 | 13.734 | 186506 | 6.86 | 100 | 1.49 | 1.44 | 1.36 | 1.35 | 1.39 | 1.38 | 1.38 | 1.4 | 1.46 | 1.44 | 2.11 | 2.02 | 27.083 | 191899 | 9.36 | 100 | 3.2 | 3.13 | 3.04 | 3.03 | 3.12 | 3.11 | 3.12 | 3.11 | 3.01 | 3.03 | 3.26 | 3.22 | 26.28 | 189923 | 9.05 | 100 | 3.12 | 3.09 | 2.96 | 3.02 | 3.03 | 2.99 | 3 | 2.94 | 2.97 | 2.93 | 3.22 | 3.04 | 26.233 | 189715 | 9.07 | 100 | 3.05 | 2.9 | 2.92 | 2.77 | 2.95 | 2.81 | 2.93 | 2.81 | 3 | 2.92 | 3.09 | 2.84 | 129.0372 | 1
2025-11-27 07:04 | 1179198 | 48 | 131 | 1179198 | 131 | 251 | 502 | 25.2915 | 24.3323 | 4912666 | 203 | 3715068 | 72 | 18400 | 0 | 17.687 | 188683 | 7.89 | 100 | 2.2 | 2.1 | 2.04 | 2.03 | 2.04 | 2.07 | 2.02 | 2 | 2.06 | 1.48 | 2.21 | 2.01 | 13.79 | 186945 | 7.03 | 100 | 1.56 | 1.35 | 1.34 | 1.35 | 1.36 | 1.41 | 1.35 | 1.43 | 1.4 | 1.4 | 2.18 | 2.03 | 13.956 | 186506 | 7.08 | 100 | 1.5 | 1.45 | 1.41 | 1.37 | 1.39 | 1.42 | 1.41 | 1.4 | 1.46 | 1.45 | 2.21 | 2.1 | 26.986 | 191900 | 9.81 | 100 | 2.97 | 2.89 | 3.09 | 3.05 | 3.14 | 3.18 | 3.16 | 3.18 | 3.13 | 3.08 | 2.97 | 2.99 | 26.96 | 189924 | 9.49 | 100 | 3.2 | 3.18 | 2.98 | 3.12 | 3.1 | 3.07 | 3.07 | 3.01 | 3.05 | 3.02 | 3.32 | 3.12 | 26.898 | 189716 | 9.51 | 100 | 3.12 | 2.99 | 2.99 | 2.85 | 3.02 | 2.87 | 3 | 2.94 | 3.06 | 3.02 | 3.16 | 2.91 | 131.1303 | 1
2025-11-27 07:05 | 1179200 | 52 | 135 | 1179200 | 135 | 258 | 516 | 25.4984 | 24.4452 | 4912670 | 207 | 3715070 | 72 | 18400 | 0 | 18.127 | 188683 | 8.17 | 100 | 2.23 | 2.14 | 2.09 | 2.09 | 2.09 | 2.12 | 2.09 | 2.05 | 2.07 | 1.53 | 2.26 | 2.06 | 14.058 | 186945 | 7.25 | 100 | 1.59 | 1.37 | 1.38 | 1.36 | 1.41 | 1.43 | 1.39 | 1.44 | 1.41 | 1.41 | 2.23 | 2.08 | 14.109 | 186506 | 7.31 | 100 | 1.52 | 1.47 | 1.42 | 1.39 | 1.41 | 1.43 | 1.42 | 1.41 | 1.48 | 1.41 | 2.27 | 2.17 | 28.586 | 191900 | 10.28 | 100 | 3.38 | 3.31 | 3.22 | 3.15 | 3.26 | 3.29 | 3.27 | 3.29 | 3.23 | 3.23 | 3.45 | 3.4 | 27.713 | 189924 | 9.97 | 100 | 3.31 | 3.27 | 3.13 | 3.19 | 3.18 | 3.16 | 3.13 | 3.12 | 3.15 | 3.09 | 3.43 | 3.22 | 27.448 | 189716 | 9.94 | 100 | 3.14 | 3.01 | 3.09 | 2.94 | 3.07 | 2.96 | 3.04 | 2.96 | 3.15 | 3.09 | 3.19 | 2.97 | 135.2298 | 1
2025-11-27 07:06 | 1179203 | 54 | 133 | 1179203 | 133 | 261 | 522 | 25.6959 | 24.5768 | 4912674 | 191 | 3715071 | 58 | 18400 | 0 | 18.393 | 188684 | 8.49 | 100 | 2.27 | 2.17 | 2.1 | 2.12 | 2.13 | 2.16 | 2.12 | 2.06 | 2.13 | 1.52 | 2.3 | 2.1 | 14.11 | 186945 | 7.49 | 100 | 1.6 | 1.37 | 1.37 | 1.37 | 1.41 | 1.42 | 1.41 | 1.44 | 1.42 | 1.38 | 2.25 | 2.09 | 14.293 | 186506 | 7.56 | 100 | 1.52 | 1.47 | 1.43 | 1.39 | 1.4 | 1.43 | 1.44 | 1.44 | 1.49 | 1.47 | 2.28 | 2.19 | 27.011 | 191901 | 10.73 | 100 | 2.57 | 2.47 | 3.29 | 3.25 | 3.34 | 3.35 | 3.33 | 3.35 | 3.3 | 3.28 | 2.5 | 2.6 | 27.009 | 189925 | 10.41 | 100 | 2.79 | 2.73 | 3.17 | 3.24 | 3.24 | 3.22 | 3.16 | 3.17 | 3.2 | 3.13 | 2.92 | 2.69 | 27.005 | 189717 | 10.41 | 100 | 2.79 | 2.66 | 3.05 | 2.91 | 3.18 | 3.02 | 3.09 | 3.01 | 3.23 | 3.15 | 2.9 | 2.7 | 133.3164 | 1
2025-11-27 07:07 | 1179205 | 54 | 130 | 1179205 | 130 | 267 | 534 | 25.9028 | 24.6991 | 4912677 | 188 | 3715072 | 58 | 18400 | 0 | 18.766 | 188684 | 8.8 | 100 | 2.33 | 2.24 | 2.17 | 2.13 | 2.19 | 2.2 | 2.17 | 2.11 | 2.18 | 1.54 | 2.35 | 2.14 | 14.271 | 186946 | 7.74 | 100 | 1.58 | 1.38 | 1.38 | 1.38 | 1.41 | 1.44 | 1.4 | 1.45 | 1.43 | 1.4 | 2.31 | 2.16 | 14.413 | 186507 | 7.8 | 100 | 1.53 | 1.48 | 1.44 | 1.4 | 1.41 | 1.45 | 1.44 | 1.45 | 1.49 | 1.48 | 2.33 | 2.24 | 25.992 | 191901 | 11.14 | 100 | 2.08 | 1.96 | 3.35 | 3.33 | 3.41 | 3.42 | 3.4 | 3.43 | 3.38 | 3.34 | 1.96 | 2.14 | 26.002 | 189925 | 10.83 | 100 | 2.3 | 2.23 | 3.22 | 3.31 | 3.3 | 3.29 | 3.22 | 3.24 | 3.27 | 3.21 | 2.42 | 2.16 | 26.022 | 189717 | 10.85 | 100 | 2.28 | 2.16 | 3.11 | 2.96 | 3.24 | 3.08 | 3.15 | 3.06 | 3.3 | 3.2 | 2.39 | 2.19 | 130.4014 | 1
2025-11-27 07:08 | 1179207 | 59 | 131 | 1179207 | 131 | 271 | 542 | 26.0909 | 24.8119 | 4912680 | 187 | 3715073 | 56 | 18400 | 0 | 19.062 | 188684 | 9.12 | 100 | 2.36 | 2.28 | 2.21 | 2.19 | 2.2 | 2.24 | 2.19 | 2.17 | 2.22 | 1.56 | 2.39 | 2.18 | 14.368 | 186946 | 7.98 | 100 | 1.55 | 1.35 | 1.39 | 1.39 | 1.43 | 1.45 | 1.37 | 1.46 | 1.44 | 1.43 | 2.34 | 2.18 | 14.592 | 186507 | 8.04 | 100 | 1.54 | 1.49 | 1.45 | 1.42 | 1.44 | 1.45 | 1.45 | 1.45 | 1.51 | 1.5 | 2.37 | 2.28 | 26.031 | 191902 | 11.6 | 100 | 1.97 | 1.85 | 3.42 | 3.38 | 3.47 | 3.48 | 3.46 | 3.48 | 3.44 | 3.4 | 1.85 | 2.04 | 25.985 | 189925 | 11.29 | 100 | 2.18 | 2.12 | 3.28 | 3.37 | 3.36 | 3.35 | 3.27 | 3.29 | 3.32 | 3.26 | 2.32 | 2.05 | 25.987 | 189718 | 11.28 | 100 | 2.17 | 2.07 | 3.16 | 3.01 | 3.3 | 3.14 | 3.2 | 3.11 | 3.35 | 3.26 | 2.28 | 2.09 | 131.4891 | 1
2025-11-27 07:09 | 1179209 | 61 | 131 | 1179209 | 131 | 276 | 552 | 26.3165 | 24.953 | 4912683 | 192 | 3715074 | 61 | 18400 | 0 | 19.423 | 188685 | 9.44 | 100 | 2.39 | 2.31 | 2.23 | 2.23 | 2.25 | 2.3 | 2.25 | 2.24 | 2.26 | 1.55 | 2.42 | 2.22 | 14.58 | 186946 | 8.2 | 100 | 1.61 | 1.39 | 1.4 | 1.4 | 1.45 | 1.47 | 1.44 | 1.47 | 1.46 | 1.44 | 2.4 | 2.26 | 14.728 | 186507 | 8.27 | 100 | 1.54 | 1.47 | 1.46 | 1.42 | 1.44 | 1.45 | 1.45 | 1.46 | 1.51 | 1.5 | 2.44 | 2.34 | 26.02 | 191902 | 12.04 | 100 | 1.87 | 1.75 | 3.46 | 3.43 | 3.51 | 3.52 | 3.52 | 3.54 | 3.5 | 3.46 | 1.73 | 1.96 | 25.997 | 189926 | 11.72 | 100 | 2.06 | 2 | 3.33 | 3.43 | 3.42 | 3.41 | 3.33 | 3.36 | 3.39 | 3.33 | 2.2 | 1.93 | 25.984 | 189718 | 11.74 | 100 | 2.03 | 1.94 | 3.22 | 3.08 | 3.37 | 3.21 | 3.27 | 3.18 | 3.43 | 3.34 | 2.15 | 1.96 | 131.5907 | 1
2025-11-27 07:10 | 1179211 | 61 | 144 | 1179212 | 142 | 280 | 560 | 26.5328 | 25.0282 | 4912686 | 212 | 3715075 | 68 | 18400 | 0 | 19.713 | 188685 | 9.76 | 100 | 2.44 | 2.36 | 2.29 | 2.29 | 2.29 | 2.33 | 2.29 | 2.28 | 2.29 | 1.56 | 2.46 | 2.26 | 14.67 | 186946 | 8.46 | 100 | 1.62 | 1.4 | 1.41 | 1.41 | 1.45 | 1.47 | 1.44 | 1.47 | 1.4 | 1.39 | 2.42 | 2.25 | 14.809 | 186507 | 8.53 | 100 | 1.55 | 1.51 | 1.47 | 1.42 | 1.44 | 1.46 | 1.45 | 1.45 | 1.52 | 1.47 | 2.44 | 2.35 | 30.577 | 191902 | 12.54 | 100 | 3.68 | 3.62 | 3.54 | 3.5 | 3.6 | 3.6 | 3.6 | 3.61 | 3.55 | 3.54 | 3.73 | 3.7 | 29.007 | 189926 | 12.22 | 100 | 3.02 | 3.57 | 3.44 | 3.45 | 3.42 | 3.42 | 3.44 | 3.43 | 3.46 | 3.34 | 3.76 | 3.52 | 29.927 | 189719 | 12.19 | 100 | 3.45 | 3.31 | 3.34 | 3.19 | 3.42 | 3.24 | 3.39 | 3.29 | 3.46 | 3.39 | 3.25 | 3.01 | 144.7566 | 1
2025-11-27 07:11 | 1179214 | 65 | 147 | 1179214 | 147 | 282 | 564 | 26.7397 | 25.1411 | 4912691 | 294 | 3715077 | 147 | 18400 | 0 | 19.928 | 188685 | 10.11 | 100 | 2.47 | 2.39 | 2.33 | 2.32 | 2.29 | 2.35 | 2.29 | 2.32 | 2.33 | 1.58 | 2.49 | 2.29 | 14.754 | 186947 | 8.71 | 100 | 1.63 | 1.42 | 1.41 | 1.39 | 1.46 | 1.47 | 1.45 | 1.48 | 1.46 | 1.46 | 2.47 | 2.33 | 14.951 | 186508 | 8.76 | 100 | 1.56 | 1.5 | 1.47 | 1.43 | 1.45 | 1.47 | 1.44 | 1.47 | 1.52 | 1.52 | 2.5 | 2.4 | 31.442 | 191903 | 13.02 | 100 | 3.7 | 3.64 | 3.59 | 3.58 | 3.66 | 3.63 | 3.68 | 3.64 | 3.59 | 3.57 | 3.81 | 3.73 | 30.495 | 189927 | 12.69 | 100 | 3.53 | 3.56 | 3.49 | 3.53 | 3.52 | 3.49 | 3.52 | 3.45 | 3.49 | 3.42 | 3.77 | 3.55 | 30.337 | 189719 | 12.71 | 100 | 3.54 | 3.39 | 3.41 | 3.24 | 3.45 | 3.29 | 3.43 | 3.37 | 3.5 | 3.43 | 3.6 | 3.32 | 147.8773 | 1
2025-11-27 07:12 | 1179216 | 68 | 149 | 1179216 | 149 | 286 | 572 | 26.9654 | 25.2821 | 4912696 | 323 | 3715080 | 174 | 18400 | 0 | 20.232 | 188686 | 10.43 | 100 | 2.5 | 2.43 | 2.36 | 2.33 | 2.37 | 2.39 | 2.33 | 2.35 | 2.38 | 1.56 | 2.53 | 2.32 | 14.84 | 186947 | 8.95 | 100 | 1.62 | 1.4 | 1.42 | 1.42 | 1.44 | 1.47 | 1.45 | 1.46 | 1.46 | 1.46 | 2.48 | 2.31 | 15.01 | 186508 | 9.01 | 100 | 1.56 | 1.51 | 1.47 | 1.44 | 1.46 | 1.46 | 1.43 | 1.47 | 1.53 | 1.53 | 2.53 | 2.43 | 31.914 | 191904 | 13.55 | 100 | 3.75 | 3.69 | 3.63 | 3.63 | 3.72 | 3.68 | 3.73 | 3.68 | 3.64 | 3.62 | 3.84 | 3.83 | 30.912 | 189927 | 13.2 | 100 | 3.58 | 3.62 | 3.54 | 3.6 | 3.58 | 3.53 | 3.52 | 3.49 | 3.53 | 3.46 | 3.82 | 3.59 | 30.748 | 189720 | 13.19 | 100 | 3.58 | 3.43 | 3.46 | 3.3 | 3.5 | 3.33 | 3.48 | 3.42 | 3.53 | 3.48 | 3.65 | 3.36 | 150.0053 | 1
2025-11-27 07:13 | 1179219 | 68 | 151 | 1179219 | 151 | 291 | 582 | 27.1723 | 25.4232 | 4912701 | 321 | 3715082 | 170 | 18400 | 0 | 20.546 | 188686 | 10.77 | 100 | 2.54 | 2.45 | 2.36 | 2.39 | 2.41 | 2.45 | 2.39 | 2.38 | 2.37 | 1.59 | 2.57 | 2.36 | 15.02 | 186947 | 9.2 | 100 | 1.64 | 1.42 | 1.43 | 1.43 | 1.46 | 1.46 | 1.47 | 1.49 | 1.45 | 1.47 | 2.54 | 2.39 | 15.155 | 186508 | 9.28 | 100 | 1.58 | 1.53 | 1.48 | 1.45 | 1.47 | 1.47 | 1.46 | 1.49 | 1.52 | 1.54 | 2.58 | 2.48 | 32.338 | 191904 | 14.11 | 100 | 3.83 | 3.78 | 3.71 | 3.68 | 3.76 | 3.72 | 3.79 | 3.73 | 3.69 | 3.68 | 3.92 | 3.89 | 31.241 | 189928 | 13.71 | 100 | 3.64 | 3.66 | 3.58 | 3.66 | 3.64 | 3.52 | 3.6 | 3.56 | 3.59 | 3.42 | 3.82 | 3.6 | 31.055 | 189720 | 13.71 | 100 | 3.64 | 3.5 | 3.44 | 3.29 | 3.55 | 3.39 | 3.53 | 3.46 | 3.57 | 3.53 | 3.64 | 3.4 | 152.1269 | 1
2025-11-27 07:14 | 1179221 | 73 | 153 | 1179222 | 153 | 296 | 592 | 27.3792 | 25.4796 | 4912706 | 324 | 3715085 | 171 | 18400 | 0 | 20.838 | 188686 | 11.11 | 100 | 2.56 | 2.48 | 2.41 | 2.43 | 2.45 | 2.47 | 2.43 | 2.42 | 2.45 | 1.59 | 2.6 | 2.39 | 15.12 | 186947 | 9.45 | 100 | 1.64 | 1.42 | 1.43 | 1.43 | 1.42 | 1.47 | 1.41 | 1.49 | 1.47 | 1.47 | 2.58 | 2.42 | 15.217 | 186508 | 9.53 | 100 | 1.53 | 1.46 | 1.48 | 1.44 | 1.47 | 1.48 | 1.48 | 1.48 | 1.54 | 1.55 | 2.62 | 2.52 | 32.911 | 191905 | 14.62 | 100 | 3.91 | 3.84 | 3.76 | 3.74 | 3.83 | 3.82 | 3.84 | 3.79 | 3.75 | 3.77 | 3.98 | 3.95 | 31.89 | 189928 | 14.27 | 100 | 3.72 | 3.76 | 3.64 | 3.71 | 3.66 | 3.65 | 3.68 | 3.58 | 3.64 | 3.58 | 3.96 | 3.72 | 31.8 | 189721 | 14.26 | 100 | 3.71 | 3.55 | 3.51 | 3.36 | 3.62 | 3.45 | 3.54 | 3.46 | 3.58 | 3.6 | 3.69 | 3.45 | 154.2515 | 1
2025-11-27 07:15 | 1179224 | 75 | 157 | 1179224 | 157 | 303 | 606 | 27.5861 | 25.5454 | 4912711 | 253 | 3715087 | 96 | 18400 | 0 | 21.301 | 188687 | 11.46 | 100 | 2.64 | 2.56 | 2.51 | 2.49 | 2.54 | 2.53 | 2.48 | 2.5 | 2.49 | 1.6 | 2.66 | 2.47 | 15.306 | 186948 | 9.7 | 100 | 1.66 | 1.44 | 1.44 | 1.44 | 1.48 | 1.49 | 1.48 | 1.48 | 1.49 | 1.49 | 2.64 | 2.49 | 15.554 | 186509 | 9.79 | 100 | 1.58 | 1.54 | 1.5 | 1.45 | 1.48 | 1.48 | 1.49 | 1.49 | 1.6 | 1.57 | 2.66 | 2.58 | 33.804 | 191905 | 15.21 | 100 | 4 | 3.96 | 3.88 | 3.85 | 3.91 | 3.94 | 3.97 | 3.85 | 3.87 | 3.87 | 4.07 | 4.05 | 32.71 | 189929 | 14.77 | 100 | 3.81 | 3.85 | 3.76 | 3.82 | 3.8 | 3.68 | 3.73 | 3.7 | 3.74 | 3.66 | 4.04 | 3.82 | 32.561 | 189721 | 14.76 | 100 | 3.8 | 3.66 | 3.65 | 3.49 | 3.71 | 3.53 | 3.69 | 3.63 | 3.75 | 3.69 | 3.86 | 3.58 | 158.3968 | 1
2025-11-27 07:16 | 1179227 | 75 | 160 | 1179227 | 159 | 309 | 618 | 27.7648 | 25.5266 | 4912716 | 244 | 3715089 | 84 | 18400 | 0 | 21.713 | 188687 | 11.83 | 100 | 2.69 | 2.61 | 2.54 | 2.52 | 2.53 | 2.58 | 2.51 | 2.54 | 2.53 | 1.62 | 2.71 | 2.5 | 15.475 | 186948 | 9.96 | 100 | 1.67 | 1.44 | 1.43 | 1.44 | 1.48 | 1.5 | 1.48 | 1.51 | 1.5 | 1.48 | 2.67 | 2.52 | 15.704 | 186509 | 10.03 | 100 | 1.59 | 1.54 | 1.51 | 1.46 | 1.49 | 1.51 | 1.5 | 1.49 | 1.65 | 1.63 | 2.7 | 2.61 | 34.27 | 191906 | 15.74 | 100 | 4.07 | 4.01 | 3.94 | 3.88 | 4.01 | 4.01 | 4.04 | 3.92 | 3.83 | 3.94 | 4.16 | 4.14 | 33.253 | 189929 | 15.32 | 100 | 3.86 | 3.87 | 3.8 | 3.88 | 3.86 | 3.85 | 3.78 | 3.78 | 3.82 | 3.66 | 4.08 | 3.85 | 33.067 | 189722 | 15.31 | 100 | 3.86 | 3.72 | 3.66 | 3.51 | 3.78 | 3.62 | 3.75 | 3.68 | 3.81 | 3.76 | 3.85 | 3.62 | 161.5228 | 1
2025-11-27 07:17 | 1179229 | 81 | 161 | 1179229 | 161 | 312 | 624 | 27.9058 | 25.4796 | 4912719 | 256 | 3715090 | 95 | 18400 | 0 | 21.92 | 188687 | 12.19 | 100 | 2.72 | 2.63 | 2.57 | 2.51 | 2.56 | 2.62 | 2.57 | 2.56 | 2.55 | 1.62 | 2.74 | 2.54 | 15.524 | 186948 | 10.22 | 100 | 1.65 | 1.44 | 1.37 | 1.46 | 1.49 | 1.51 | 1.49 | 1.5 | 1.5 | 1.5 | 2.71 | 2.56 | 15.754 | 186509 | 10.31 | 100 | 1.59 | 1.54 | 1.46 | 1.47 | 1.5 | 1.46 | 1.48 | 1.51 | 1.65 | 1.64 | 2.76 | 2.66 | 34.592 | 191906 | 16.32 | 100 | 4.11 | 4.05 | 3.96 | 3.97 | 4.03 | 4.05 | 4.06 | 3.92 | 3.98 | 3.97 | 4.12 | 4.12 | 33.582 | 189930 | 15.88 | 100 | 3.89 | 3.91 | 3.83 | 3.92 | 3.89 | 3.89 | 3.8 | 3.82 | 3.85 | 3.69 | 4.1 | 3.89 | 33.316 | 189722 | 15.86 | 100 | 3.9 | 3.75 | 3.8 | 3.55 | 3.75 | 3.56 | 3.82 | 3.75 | 3.9 | 3.74 | 3.99 | 3.7 | 162.6113 | 1
2025-11-27 07:18 | 1179232 | 83 | 164 | 1179232 | 164 | 319 | 638 | 28.0469 | 25.5924 | 4912724 | 313 | 3715092 | 149 | 18400 | 0 | 22.374 | 188688 | 12.56 | 100 | 2.76 | 2.69 | 2.6 | 2.6 | 2.62 | 2.66 | 2.63 | 2.62 | 2.64 | 1.63 | 2.8 | 2.58 | 15.662 | 186948 | 10.48 | 100 | 1.67 | 1.45 | 1.45 | 1.4 | 1.51 | 1.52 | 1.49 | 1.52 | 1.51 | 1.5 | 2.77 | 2.62 | 15.976 | 186509 | 10.57 | 100 | 1.6 | 1.55 | 1.49 | 1.47 | 1.51 | 1.5 | 1.5 | 1.51 | 1.66 | 1.65 | 2.82 | 2.72 | 35.381 | 191907 | 16.93 | 100 | 4.15 | 4.1 | 4.06 | 4.06 | 4.14 | 4.13 | 4.15 | 4.1 | 4.03 | 4.07 | 4.26 | 4.24 | 34.135 | 189931 | 16.44 | 100 | 3.99 | 4.01 | 3.93 | 3.97 | 4.01 | 3.97 | 3.93 | 3.91 | 3.94 | 3.74 | 4.15 | 3.93 | 34.017 | 189723 | 16.42 | 100 | 3.97 | 3.84 | 3.87 | 3.62 | 3.91 | 3.72 | 3.8 | 3.72 | 3.96 | 3.88 | 3.95 | 3.71 | 165.7218 | 1
2025-11-27 07:19 | 1179235 | 83 | 166 | 1179235 | 166 | 323 | 646 | 28.1597 | 25.6677 | 4912730 | 292 | 3715095 | 126 | 18400 | 0 | 22.734 | 188688 | 12.96 | 100 | 2.82 | 2.75 | 2.67 | 2.61 | 2.66 | 2.71 | 2.64 | 2.68 | 2.66 | 1.63 | 2.83 | 2.63 | 15.85 | 186949 | 10.74 | 100 | 1.68 | 1.46 | 1.46 | 1.47 | 1.52 | 1.53 | 1.51 | 1.52 | 1.51 | 1.5 | 2.81 | 2.66 | 16.106 | 186510 | 10.84 | 100 | 1.61 | 1.56 | 1.51 | 1.47 | 1.5 | 1.52 | 1.54 | 1.52 | 1.68 | 1.64 | 2.86 | 2.76 | 35.911 | 191907 | 17.49 | 100 | 4.2 | 4.15 | 4.14 | 4.08 | 4.18 | 4.19 | 4.23 | 4.18 | 4.08 | 4.13 | 4.32 | 4.32 | 34.808 | 189931 | 17.05 | 100 | 4.06 | 4.12 | 4.01 | 4.03 | 4.08 | 4.04 | 4.02 | 3.95 | 3.98 | 3.93 | 4.29 | 4.05 | 34.714 | 189723 | 17.03 | 100 | 4.04 | 3.9 | 3.94 | 3.74 | 3.97 | 3.76 | 3.93 | 3.87 | 4.04 | 3.94 | 4.02 | 3.77 | 167.8081 | 1
2025-11-27 07:20 | 1179238 | 89 | 167 | 1179238 | 168 | 326 | 652 | 28.2914 | 25.7617 | 4912735 | 299 | 3715097 | 132 | 18400 | 0 | 22.962 | 188688 | 13.32 | 100 | 2.85 | 2.77 | 2.7 | 2.67 | 2.71 | 2.76 | 2.7 | 2.69 | 2.69 | 1.64 | 2.88 | 2.66 | 15.963 | 186949 | 11.01 | 100 | 1.68 | 1.46 | 1.46 | 1.47 | 1.55 | 1.52 | 1.51 | 1.52 | 1.52 | 1.51 | 2.83 | 2.66 | 16.229 | 186510 | 11.12 | 100 | 1.61 | 1.56 | 1.51 | 1.49 | 1.52 | 1.52 | 1.55 | 1.53 | 1.69 | 1.67 | 2.9 | 2.8 | 36.165 | 191908 | 18.13 | 100 | 4.22 | 4.18 | 4.14 | 4.11 | 4.21 | 4.22 | 4.26 | 4.22 | 4.11 | 4.16 | 4.35 | 4.34 | 35.094 | 189932 | 17.66 | 100 | 4.11 | 4.15 | 4.06 | 4.09 | 4.12 | 4.07 | 4.05 | 4.02 | 4.05 | 3.97 | 4.37 | 4.12 | 35.029 | 189724 | 17.64 | 100 | 4.09 | 3.94 | 3.99 | 3.75 | 4.03 | 3.83 | 4 | 3.9 | 4.09 | 3.97 | 4.17 | 3.87 | 168.8956 | 1
2025-11-27 07:21 | 1179240 | 92 | 167 | 1179241 | 167 | 325 | 650 | 28.423 | 25.7523 | 4912739 | 293 | 3715099 | 126 | 18400 | 0 | 23.01 | 188689 | 13.72 | 100 | 2.85 | 2.78 | 2.71 | 2.7 | 2.72 | 2.77 | 2.7 | 2.71 | 2.7 | 1.64 | 2.88 | 2.65 | 15.955 | 186949 | 11.27 | 100 | 1.69 | 1.46 | 1.46 | 1.48 | 1.54 | 1.53 | 1.52 | 1.53 | 1.52 | 1.52 | 2.83 | 2.67 | 16.284 | 186510 | 11.38 | 100 | 1.62 | 1.56 | 1.5 | 1.48 | 1.52 | 1.53 | 1.53 | 1.53 | 1.7 | 1.69 | 2.88 | 2.8 | 35.929 | 191909 | 18.7 | 100 | 4.2 | 4.15 | 4.15 | 4.1 | 4.2 | 4.19 | 4.21 | 4.2 | 4.08 | 4.14 | 4.31 | 4.31 | 34.864 | 189932 | 18.21 | 100 | 4.08 | 4.11 | 4.02 | 4.02 | 4.1 | 4.05 | 4.06 | 3.95 | 4.02 | 3.95 | 4.31 | 4.08 | 34.843 | 189725 | 18.19 | 100 | 4.05 | 3.91 | 3.97 | 3.75 | 4.01 | 3.82 | 3.95 | 3.89 | 4.07 | 3.99 | 4.16 | 3.88 | 168.9723 | 1
2025-11-27 07:22 | 1179243 | 92 | 165 | 1179243 | 164 | 318 | 636 | 28.5359 | 25.884 | 4912744 | 298 | 3715101 | 133 | 18400 | 0 | 22.766 | 188689 | 14.1 | 100 | 2.83 | 2.75 | 2.67 | 2.66 | 2.68 | 2.73 | 2.67 | 2.67 | 2.69 | 1.64 | 2.85 | 2.63 | 15.971 | 186949 | 11.54 | 100 | 1.69 | 1.46 | 1.47 | 1.48 | 1.57 | 1.53 | 1.52 | 1.53 | 1.52 | 1.53 | 2.81 | 2.66 | 16.299 | 186510 | 11.63 | 100 | 1.62 | 1.56 | 1.53 | 1.49 | 1.52 | 1.53 | 1.55 | 1.53 | 1.72 | 1.7 | 2.87 | 2.75 | 35.075 | 191909 | 19.3 | 100 | 4.22 | 4.14 | 4.07 | 3.97 | 4.07 | 4.12 | 4.14 | 4.09 | 3.98 | 4.04 | 4.25 | 4.23 | 34.221 | 189933 | 18.79 | 100 | 4 | 4.02 | 3.94 | 4.02 | 4.01 | 3.98 | 3.98 | 3.87 | 3.96 | 3.89 | 4.21 | 3.99 | 34.252 | 189725 | 18.77 | 100 | 4 | 3.86 | 3.89 | 3.71 | 3.94 | 3.76 | 3.87 | 3.82 | 3.99 | 3.88 | 4.07 | 3.79 | 167.0138 | 1
2025-11-27 07:23 | 1179246 | 97 | 163 | 1179246 | 163 | 316 | 632 | 28.6487 | 25.9028 | 4912749 | 259 | 3715103 | 96 | 18400 | 0 | 22.731 | 188690 | 14.46 | 100 | 2.84 | 2.76 | 2.66 | 2.66 | 2.68 | 2.71 | 2.64 | 2.66 | 2.68 | 1.64 | 2.83 | 2.62 | 15.958 | 186950 | 11.8 | 100 | 1.69 | 1.46 | 1.47 | 1.48 | 1.56 | 1.53 | 1.51 | 1.53 | 1.53 | 1.52 | 2.81 | 2.65 | 16.336 | 186511 | 11.9 | 100 | 1.62 | 1.57 | 1.52 | 1.48 | 1.51 | 1.53 | 1.56 | 1.53 | 1.71 | 1.83 | 2.86 | 2.76 | 34.707 | 191910 | 19.88 | 100 | 4.18 | 4.09 | 4.02 | 3.97 | 4.05 | 4.08 | 4.08 | 4 | 3.99 | 4.03 | 4.22 | 4.19 | 33.788 | 189933 | 19.35 | 100 | 3.95 | 3.95 | 3.9 | 3.99 | 3.96 | 3.93 | 3.94 | 3.79 | 3.9 | 3.84 | 4.21 | 3.97 | 33.882 | 189726 | 19.33 | 100 | 3.96 | 3.82 | 3.83 | 3.67 | 3.88 | 3.71 | 3.87 | 3.8 | 3.96 | 3.88 | 4.02 | 3.74 | 165.0536 | 1
2025-11-27 07:24 | 1179249 | 100 | 163 | 1179249 | 164 | 316 | 632 | 28.7522 | 25.978 | 4912753 | 267 | 3715104 | 104 | 18400 | 0 | 22.82 | 188690 | 14.84 | 100 | 2.84 | 2.76 | 2.71 | 2.65 | 2.69 | 2.69 | 2.67 | 2.66 | 2.69 | 1.64 | 2.87 | 2.64 | 15.972 | 186950 | 12.05 | 100 | 1.7 | 1.47 | 1.47 | 1.49 | 1.55 | 1.54 | 1.52 | 1.54 | 1.52 | 1.52 | 2.81 | 2.64 | 16.641 | 186511 | 12.19 | 100 | 1.62 | 1.57 | 1.51 | 1.48 | 1.52 | 1.53 | 1.54 | 1.53 | 1.76 | 2.22 | 2.86 | 2.75 | 34.712 | 191910 | 20.49 | 100 | 4.11 | 4.1 | 4.02 | 3.95 | 4.1 | 4.08 | 4.08 | 4.04 | 4.02 | 4.01 | 4.17 | 4.16 | 33.717 | 189934 | 19.92 | 100 | 3.98 | 4.01 | 3.89 | 3.97 | 3.96 | 3.92 | 3.92 | 3.8 | 3.89 | 3.83 | 4.16 | 3.92 | 33.607 | 189726 | 19.9 | 100 | 3.95 | 3.81 | 3.86 | 3.66 | 3.87 | 3.69 | 3.79 | 3.74 | 3.91 | 3.8 | 4.01 | 3.72 | 165.1126 | 1
2025-11-27 07:25 | 1179252 | 100 | 166 | 1179252 | 166 | 320 | 640 | 28.8462 | 25.9404 | 4912758 | 288 | 3715106 | 122 | 18400 | 0 | 23.131 | 188690 | 15.22 | 100 | 2.91 | 2.83 | 2.73 | 2.73 | 2.74 | 2.79 | 2.74 | 2.7 | 2.7 | 1.65 | 2.91 | 2.69 | 16.078 | 186950 | 12.33 | 100 | 1.7 | 1.48 | 1.46 | 1.49 | 1.57 | 1.54 | 1.53 | 1.54 | 1.53 | 1.49 | 2.86 | 2.7 | 17.172 | 186511 | 12.47 | 100 | 1.63 | 1.57 | 1.52 | 1.49 | 1.52 | 1.54 | 1.55 | 1.54 | 2.16 | 2.6 | 2.9 | 2.79 | 35.157 | 191911 | 21.04 | 100 | 4.22 | 4.15 | 4.08 | 3.96 | 4.13 | 4.13 | 4.15 | 4.09 | 4.07 | 4.07 | 4.26 | 4.25 | 34.12 | 189935 | 20.48 | 100 | 4.03 | 4.06 | 3.97 | 4.02 | 4.03 | 3.94 | 3.97 | 3.89 | 3.95 | 3.86 | 4.18 | 3.95 | 33.896 | 189727 | 20.46 | 100 | 3.99 | 3.85 | 3.9 | 3.69 | 3.91 | 3.72 | 3.83 | 3.78 | 3.98 | 3.83 | 4.05 | 3.76 | 168.2061 | 1
2025-11-27 07:26 | 1179254 | 106 | 168 | 1179254 | 168 | 325 | 650 | 28.959 | 26.0909 | 4912763 | 299 | 3715109 | 131 | 18400 | 0 | 23.435 | 188691 | 15.61 | 100 | 2.94 | 2.87 | 2.77 | 2.77 | 2.78 | 2.79 | 2.78 | 2.75 | 2.81 | 1.66 | 2.97 | 2.75 | 16.113 | 186950 | 12.59 | 100 | 1.7 | 1.48 | 1.48 | 1.41 | 1.58 | 1.55 | 1.52 | 1.47 | 1.54 | 1.54 | 2.91 | 2.74 | 17.605 | 186512 | 12.76 | 100 | 1.64 | 1.58 | 1.53 | 1.5 | 1.51 | 1.51 | 1.57 | 1.55 | 2.73 | 2.69 | 2.95 | 2.84 | 35.681 | 191912 | 21.66 | 100 | 4.28 | 4.21 | 4.13 | 4.05 | 4.16 | 4.2 | 4.21 | 4.15 | 4.14 | 4.11 | 4.28 | 4.28 | 34.671 | 189935 | 21.08 | 100 | 4.08 | 4.12 | 4.02 | 4.08 | 4.09 | 4 | 4.02 | 3.95 | 4 | 3.93 | 4.28 | 4.04 | 34.508 | 189727 | 21.03 | 100 | 4.06 | 3.91 | 3.96 | 3.71 | 3.98 | 3.8 | 3.89 | 3.83 | 4.04 | 3.9 | 4.12 | 3.82 | 170.2991 | 1
2025-11-27 07:27 | 1179257 | 108 | 172 | 1179257 | 172 | 334 | 668 | 29.1001 | 26.2131 | 4912768 | 289 | 3715111 | 117 | 18400 | 0 | 23.954 | 188691 | 16.02 | 100 | 3.02 | 2.94 | 2.83 | 2.84 | 2.84 | 2.87 | 2.85 | 2.82 | 2.82 | 1.67 | 3.01 | 2.78 | 16.366 | 186951 | 12.89 | 100 | 1.72 | 1.49 | 1.48 | 1.49 | 1.58 | 1.55 | 1.54 | 1.55 | 1.55 | 1.54 | 2.97 | 2.8 | 17.801 | 186512 | 13.07 | 100 | 1.64 | 1.59 | 1.54 | 1.46 | 1.51 | 1.55 | 1.58 | 1.54 | 2.8 | 2.75 | 3.02 | 2.91 | 36.656 | 191912 | 22.26 | 100 | 4.39 | 4.31 | 4.23 | 4.21 | 4.3 | 4.31 | 4.34 | 4.27 | 4.24 | 4.22 | 4.46 | 4.44 | 35.389 | 189936 | 21.63 | 100 | 4.11 | 4.09 | 4.09 | 4.19 | 4.18 | 4.1 | 4.14 | 4.03 | 4.08 | 4.02 | 4.41 | 4.16 | 35.378 | 189728 | 21.61 | 100 | 4.15 | 4.01 | 4.06 | 3.84 | 4.06 | 3.88 | 4.05 | 3.98 | 4.15 | 4.05 | 4.21 | 3.92 | 174.4389 | 1
2025-11-27 07:28 | 1179260 | 108 | 174 | 1179260 | 175 | 337 | 674 | 29.2318 | 26.3636 | 4912773 | 287 | 3715113 | 113 | 18400 | 0 | 24.224 | 188692 | 16.4 | 100 | 2.95 | 2.98 | 2.87 | 2.88 | 2.91 | 2.94 | 2.89 | 2.86 | 2.93 | 1.68 | 3.07 | 2.86 | 16.433 | 186951 | 13.14 | 100 | 1.76 | 1.52 | 1.52 | 1.5 | 1.59 | 1.56 | 1.54 | 1.56 | 1.5 | 1.56 | 3.01 | 2.85 | 18.115 | 186512 | 13.36 | 100 | 1.63 | 1.57 | 1.55 | 1.5 | 1.54 | 1.54 | 1.59 | 1.54 | 2.86 | 2.77 | 3.06 | 2.96 | 37.101 | 191913 | 22.87 | 100 | 4.44 | 4.37 | 4.29 | 4.25 | 4.4 | 4.37 | 4.36 | 4.31 | 4.31 | 4.24 | 4.44 | 4.46 | 36.089 | 189936 | 22.26 | 100 | 4.25 | 4.29 | 4.15 | 4.25 | 4.26 | 4.17 | 4.19 | 4.12 | 4.15 | 4.08 | 4.47 | 4.23 | 36.076 | 189729 | 22.17 | 100 | 4.18 | 4.06 | 4.14 | 3.92 | 4.14 | 3.95 | 4.12 | 4.06 | 4.23 | 4.13 | 4.3 | 4.02 | 176.5477 | 1
2025-11-27 07:29 | 1179263 | 114 | 175 | 1179263 | 175 | 338 | 676 | 29.4011 | 26.373 | 4912778 | 276 | 3715115 | 101 | 18400 | 0 | 24.374 | 188692 | 16.8 | 100 | 2.97 | 2.99 | 2.88 | 2.89 | 2.9 | 2.96 | 2.91 | 2.9 | 2.91 | 1.69 | 3.05 | 2.84 | 16.495 | 186951 | 13.43 | 100 | 1.76 | 1.52 | 1.54 | 1.51 | 1.59 | 1.56 | 1.55 | 1.55 | 1.55 | 1.55 | 3.03 | 2.85 | 18.161 | 186512 | 13.66 | 100 | 1.64 | 1.57 | 1.55 | 1.51 | 1.54 | 1.54 | 1.6 | 1.54 | 2.87 | 2.82 | 3.07 | 2.96 | 37.106 | 191913 | 23.49 | 100 | 4.38 | 4.34 | 4.3 | 4.21 | 4.4 | 4.38 | 4.27 | 4.31 | 4.32 | 4.28 | 4.43 | 4.43 | 36.048 | 189937 | 22.85 | 100 | 4.25 | 4.3 | 4.19 | 4.26 | 4.23 | 4.19 | 4.19 | 4.15 | 4.16 | 4.1 | 4.43 | 4.2 | 35.974 | 189729 | 22.84 | 100 | 4.22 | 4.08 | 4.14 | 3.86 | 4.17 | 3.97 | 4.06 | 3.99 | 4.23 | 4.08 | 4.27 | 3.99 | 177.6664 | 1
2025-11-27 07:30 | 1179266 | 117 | 171 | 1179266 | 170 | 337 | 674 | 29.5233 | 26.5046 | 4912782 | 247 | 3715116 | 76 | 18400 | 0 | 24.422 | 188692 | 17.21 | 100 | 3.03 | 3.01 | 2.92 | 2.88 | 2.9 | 2.96 | 2.91 | 2.88 | 2.93 | 1.68 | 3.09 | 2.88 | 16.598 | 186952 | 13.69 | 100 | 1.77 | 1.54 | 1.54 | 1.51 | 1.59 | 1.56 | 1.56 | 1.56 | 1.55 | 1.55 | 3.03 | 2.86 | 18.18 | 186513 | 13.96 | 100 | 1.61 | 1.56 | 1.56 | 1.51 | 1.56 | 1.54 | 1.61 | 1.55 | 2.88 | 2.83 | 3.07 | 2.97 | 34.978 | 191914 | 24.1 | 100 | 3.48 | 3.45 | 4.27 | 4.28 | 4.34 | 4.36 | 4.32 | 4.34 | 4.31 | 4.29 | 3.44 | 3.54 | 34.991 | 189938 | 23.45 | 100 | 3.76 | 3.78 | 4.23 | 4.24 | 4.25 | 4.16 | 4.18 | 4.15 | 4.17 | 4.1 | 3.95 | 3.69 | 35.019 | 189730 | 23.4 | 100 | 3.72 | 3.63 | 4.14 | 3.83 | 4.13 | 3.96 | 4.05 | 3.98 | 4.23 | 4.07 | 3.9 | 3.66 | 173.6789 | 1
2025-11-27 07:31 | 1179269 | 117 | 173 | 1179269 | 173 | 334 | 668 | 29.6926 | 26.5799 | 4912786 | 252 | 3715117 | 79 | 18400 | 0 | 24.273 | 188693 | 17.61 | 100 | 3.01 | 3 | 2.87 | 2.88 | 2.93 | 2.97 | 2.89 | 2.86 | 2.91 | 1.69 | 3.08 | 2.86 | 16.634 | 186952 | 13.97 | 100 | 1.77 | 1.55 | 1.55 | 1.52 | 1.59 | 1.57 | 1.56 | 1.56 | 1.61 | 1.57 | 3.02 | 2.84 | 18.252 | 186513 | 14.28 | 100 | 1.65 | 1.59 | 1.55 | 1.58 | 1.55 | 1.61 | 1.62 | 1.55 | 2.88 | 2.82 | 3.06 | 2.95 | 36.497 | 191915 | 24.7 | 100 | 4.41 | 4.32 | 4.25 | 4.25 | 4.34 | 4.32 | 4.35 | 4.18 | 4.26 | 4.15 | 4.41 | 4.4 | 35.745 | 189938 | 24.04 | 100 | 4.21 | 4.23 | 4.14 | 4.2 | 4.21 | 4.12 | 4.14 | 4.1 | 4.1 | 4.04 | 4.4 | 4.17 | 35.66 | 189730 | 24.03 | 100 | 4.19 | 4.04 | 4.03 | 3.9 | 4.09 | 3.91 | 4.11 | 4.03 | 4.16 | 4.11 | 4.22 | 3.95 | 175.8133 | 1
2025-11-27 07:32 | 1179272 | 123 | 174 | 1179272 | 174 | 336 | 672 | 29.843 | 26.5987 | 4912790 | 249 | 3715118 | 75 | 18400 | 0 | 24.561 | 188693 | 18.02 | 100 | 3.03 | 3.03 | 2.94 | 2.9 | 2.95 | 2.98 | 2.89 | 2.9 | 2.95 | 1.7 | 3.08 | 2.89 | 16.76 | 186952 | 14.24 | 100 | 1.78 | 1.56 | 1.56 | 1.51 | 1.59 | 1.57 | 1.64 | 1.56 | 1.62 | 1.62 | 3.04 | 2.87 | 18.346 | 186513 | 14.56 | 100 | 1.63 | 1.57 | 1.57 | 1.58 | 1.57 | 1.6 | 1.63 | 1.62 | 2.89 | 2.84 | 3.09 | 2.97 | 35.967 | 191915 | 25.3 | 100 | 3.92 | 3.88 | 4.25 | 4.26 | 4.38 | 4.33 | 4.31 | 4.28 | 4.28 | 4.27 | 3.9 | 3.95 | 35.892 | 189939 | 24.64 | 100 | 4.23 | 4.27 | 4.16 | 4.23 | 4.24 | 4.17 | 4.16 | 4.12 | 4.12 | 3.99 | 4.44 | 4.19 | 35.735 | 189731 | 24.59 | 100 | 4.2 | 4.06 | 4.04 | 3.91 | 4.13 | 3.92 | 4.12 | 4.04 | 4.16 | 4.11 | 4.24 | 3.95 | 176.9218 | 1
2025-11-27 07:33 | 1179274 | 126 | 174 | 1179275 | 174 | 338 | 676 | 29.9747 | 26.6269 | 4912794 | 247 | 3715120 | 73 | 18400 | 0 | 24.671 | 188694 | 18.46 | 100 | 3.05 | 3.05 | 2.95 | 2.92 | 2.97 | 3.01 | 2.95 | 2.92 | 2.95 | 1.69 | 3.12 | 2.9 | 16.8 | 186952 | 14.54 | 100 | 1.77 | 1.56 | 1.57 | 1.53 | 1.61 | 1.58 | 1.64 | 1.58 | 1.63 | 1.63 | 3.08 | 2.91 | 18.554 | 186514 | 14.89 | 100 | 1.67 | 1.61 | 1.62 | 1.59 | 1.56 | 1.64 | 1.64 | 1.64 | 2.92 | 2.87 | 3.11 | 3 | 36.034 | 191916 | 25.93 | 100 | 3.89 | 3.85 | 4.26 | 4.28 | 4.4 | 4.35 | 4.32 | 4.29 | 4.3 | 4.29 | 3.86 | 3.92 | 36.017 | 189939 | 25.19 | 100 | 4.25 | 4.29 | 4.2 | 4.25 | 4.26 | 4.17 | 4.2 | 4.14 | 4.08 | 4.01 | 4.46 | 4.21 | 35.953 | 189732 | 25.18 | 100 | 4.18 | 4.04 | 4.07 | 3.93 | 4.07 | 3.94 | 4.12 | 4.06 | 4.21 | 4.14 | 4.25 | 3.97 | 177.0026 | 1
2025-11-27 07:34 | 1179277 | 126 | 175 | 1179278 | 178 | 344 | 688 | 30.1063 | 26.7303 | 4912798 | 252 | 3715121 | 77 | 18400 | 0 | 25.129 | 188694 | 18.87 | 100 | 3.13 | 3.1 | 2.97 | 2.99 | 3.04 | 3.08 | 3 | 2.99 | 3.03 | 1.72 | 3.18 | 2.96 | 16.938 | 186953 | 14.81 | 100 | 1.79 | 1.56 | 1.56 | 1.42 | 1.61 | 1.59 | 1.65 | 1.64 | 1.64 | 1.64 | 3.12 | 2.94 | 18.74 | 186514 | 15.18 | 100 | 1.68 | 1.62 | 1.63 | 1.55 | 1.61 | 1.64 | 1.64 | 1.65 | 2.97 | 2.93 | 3.16 | 3.05 | 36.003 | 191916 | 26.5 | 100 | 3.66 | 3.63 | 4.35 | 4.37 | 4.49 | 4.44 | 4.4 | 4.38 | 4.38 | 4.37 | 3.62 | 3.71 | 35.984 | 189940 | 25.83 | 100 | 3.99 | 4.02 | 4.26 | 4.34 | 4.34 | 4.25 | 4.26 | 4.22 | 4.21 | 4.14 | 4.22 | 3.97 | 35.975 | 189732 | 25.81 | 100 | 3.91 | 3.82 | 4.2 | 3.99 | 4.24 | 4.02 | 4.19 | 4.14 | 4.31 | 4.2 | 4.04 | 3.8 | 178.1012 | 1
2025-11-27 07:35 | 1179280 | 131 | 180 | 1179280 | 180 | 356 | 712 | 30.2286 | 26.7679 | 4912802 | 255 | 3715122 | 75 | 18400 | 0 | 25.953 | 188694 | 19.29 | 100 | 3.2 | 3.2 | 3.11 | 3.08 | 3.13 | 3.17 | 3.1 | 3.07 | 3.12 | 1.73 | 3.27 | 3.06 | 17.244 | 186953 | 15.11 | 100 | 1.79 | 1.57 | 1.58 | 1.56 | 1.62 | 1.59 | 1.65 | 1.65 | 1.64 | 1.63 | 3.21 | 3.04 | 19.088 | 186514 | 15.51 | 100 | 1.71 | 1.65 | 1.64 | 1.6 | 1.62 | 1.65 | 1.64 | 1.66 | 3.06 | 3.02 | 3.28 | 3.16 | 37.014 | 191917 | 27.14 | 100 | 3.67 | 3.63 | 4.52 | 4.54 | 4.66 | 4.61 | 4.57 | 4.55 | 4.55 | 4.54 | 3.61 | 3.73 | 36.999 | 189941 | 26.4 | 100 | 4 | 4.03 | 4.42 | 4.51 | 4.5 | 4.4 | 4.41 | 4.37 | 4.36 | 4.29 | 4.19 | 3.94 | 36.987 | 189733 | 26.39 | 100 | 3.87 | 3.79 | 4.35 | 4.13 | 4.39 | 4.17 | 4.35 | 4.28 | 4.46 | 4.36 | 4.05 | 3.82 | 183.2676 | 1
2025-11-27 07:36 | 1179283 | 134 | 184 | 1179284 | 184 | 365 | 730 | 30.3226 | 26.7679 | 4912806 | 254 | 3715123 | 70 | 18400 | 0 | 26.609 | 188695 | 19.71 | 100 | 3.3 | 3.29 | 3.21 | 3.17 | 3.22 | 3.25 | 3.19 | 3.15 | 3.21 | 1.74 | 3.38 | 3.14 | 17.51 | 186953 | 15.4 | 100 | 1.8 | 1.57 | 1.59 | 1.58 | 1.62 | 1.65 | 1.62 | 1.65 | 1.65 | 1.64 | 3.29 | 3.09 | 19.431 | 186515 | 15.81 | 100 | 1.73 | 1.66 | 1.64 | 1.6 | 1.64 | 1.66 | 1.65 | 1.66 | 3.16 | 3.08 | 3.34 | 3.22 | 38.002 | 191918 | 27.71 | 100 | 3.77 | 3.74 | 4.63 | 4.66 | 4.78 | 4.73 | 4.69 | 4.66 | 4.66 | 4.65 | 3.72 | 3.84 | 37.994 | 189941 | 27.04 | 100 | 4.09 | 4.12 | 4.54 | 4.63 | 4.62 | 4.51 | 4.52 | 4.49 | 4.47 | 4.4 | 4.29 | 4.04 | 37.994 | 189733 | 27.03 | 100 | 4.01 | 3.93 | 4.45 | 4.23 | 4.5 | 4.26 | 4.44 | 4.38 | 4.55 | 4.45 | 4.2 | 3.95 | 187.4013 | 1
2025-11-27 07:37 | 1179286 | 134 | 185 | 1179287 | 182 | 373 | 746 | 30.4449 | 26.862 | 4912811 | 256 | 3715125 | 71 | 18400 | 0 | 27.2 | 188695 | 20.16 | 100 | 3.39 | 3.36 | 3.29 | 3.25 | 3.3 | 3.34 | 3.24 | 3.23 | 3.21 | 1.77 | 3.46 | 3.23 | 17.656 | 186954 | 15.67 | 100 | 1.81 | 1.58 | 1.56 | 1.6 | 1.63 | 1.66 | 1.67 | 1.62 | 1.65 | 1.65 | 3.38 | 3.18 | 19.676 | 186515 | 16.16 | 100 | 1.75 | 1.68 | 1.66 | 1.61 | 1.65 | 1.67 | 1.67 | 1.68 | 3.21 | 3.16 | 3.41 | 3.3 | 37.016 | 191918 | 28.35 | 100 | 3.19 | 3.15 | 4.75 | 4.78 | 4.82 | 4.85 | 4.89 | 4.77 | 4.78 | 4.75 | 3.1 | 3.29 | 36.979 | 189942 | 27.67 | 100 | 3.46 | 3.53 | 4.64 | 4.72 | 4.73 | 4.63 | 4.62 | 4.59 | 4.57 | 4.5 | 3.66 | 3.42 | 36.99 | 189734 | 27.67 | 100 | 3.41 | 3.39 | 4.55 | 4.32 | 4.59 | 4.36 | 4.53 | 4.48 | 4.65 | 4.54 | 3.6 | 3.38 | 188.4999 | 1
2025-11-27 07:38 | 1179290 | 140 | 187 | 1179290 | 187 | 383 | 766 | 30.5765 | 26.8808 | 4912816 | 263 | 3715126 | 76 | 18400 | 0 | 27.945 | 188696 | 20.61 | 100 | 3.47 | 3.43 | 3.36 | 3.34 | 3.38 | 3.43 | 3.35 | 3.32 | 3.41 | 1.79 | 3.54 | 3.3 | 17.991 | 186954 | 15.98 | 100 | 1.82 | 1.58 | 1.6 | 1.59 | 1.63 | 1.67 | 1.68 | 1.67 | 1.64 | 1.67 | 3.46 | 3.25 | 20.04 | 186515 | 16.47 | 100 | 1.77 | 1.69 | 1.67 | 1.63 | 1.66 | 1.69 | 1.64 | 1.69 | 3.31 | 3.27 | 3.52 | 3.4 | 38.034 | 191919 | 28.99 | 100 | 3.27 | 3.25 | 4.87 | 4.91 | 4.95 | 4.98 | 5.03 | 4.95 | 4.84 | 4.89 | 3.18 | 3.38 | 37.989 | 189942 | 28.31 | 100 | 3.51 | 3.6 | 4.74 | 4.79 | 4.87 | 4.77 | 4.77 | 4.75 | 4.72 | 4.64 | 3.72 | 3.48 | 37.982 | 189735 | 28.3 | 100 | 3.44 | 3.43 | 4.71 | 4.37 | 4.76 | 4.5 | 4.69 | 4.62 | 4.82 | 4.7 | 3.64 | 3.43 | 190.6249 | 1
2025-11-27 07:39 | 1179293 | 144 | 191 | 1179293 | 188 | 389 | 778 | 30.727 | 26.9372 | 4912820 | 263 | 3715127 | 72 | 18400 | 0 | 28.205 | 188696 | 21.1 | 100 | 3.56 | 3.52 | 3.39 | 3.41 | 3.45 | 3.48 | 3.4 | 3.37 | 3.45 | 1.69 | 3.6 | 3.35 | 18.188 | 186954 | 16.27 | 100 | 1.84 | 1.61 | 1.62 | 1.61 | 1.65 | 1.68 | 1.69 | 1.67 | 1.68 | 1.67 | 3.52 | 3.31 | 20.299 | 186516 | 16.82 | 100 | 1.76 | 1.69 | 1.68 | 1.64 | 1.66 | 1.7 | 1.67 | 1.7 | 3.36 | 3.33 | 3.57 | 3.46 | 38.823 | 191920 | 29.62 | 100 | 3.47 | 3.45 | 4.94 | 4.99 | 5.02 | 5.05 | 5.11 | 5.04 | 4.9 | 4.97 | 3.4 | 3.58 | 38.989 | 189943 | 28.94 | 100 | 3.76 | 3.83 | 4.8 | 4.86 | 4.95 | 4.83 | 4.83 | 4.81 | 4.79 | 4.7 | 3.97 | 3.72 | 38.978 | 189735 | 28.9 | 100 | 3.69 | 3.66 | 4.77 | 4.43 | 4.82 | 4.55 | 4.76 | 4.68 | 4.89 | 4.77 | 3.89 | 3.66 | 194.8043 | 1
2025-11-27 07:40 | 1179296 | 144 | 188 | 1179296 | 189 | 391 | 782 | 30.9057 | 27.1629 | 4912824 | 264 | 3715128 | 76 | 18400 | 0 | 28.561 | 188697 | 21.58 | 100 | 3.54 | 3.55 | 3.45 | 3.41 | 3.42 | 3.48 | 3.43 | 3.39 | 3.43 | 1.84 | 3.6 | 3.37 | 18.393 | 186954 | 16.57 | 100 | 1.84 | 1.61 | 1.58 | 1.61 | 1.66 | 1.69 | 1.69 | 1.69 | 1.69 | 1.68 | 3.55 | 3.36 | 20.441 | 186516 | 17.14 | 100 | 1.78 | 1.7 | 1.69 | 1.65 | 1.56 | 1.71 | 1.67 | 1.71 | 3.4 | 3.3 | 3.59 | 3.48 | 37.986 | 191920 | 30.26 | 100 | 3.1 | 3.07 | 4.95 | 5.02 | 5.02 | 5.06 | 5.12 | 5.05 | 4.91 | 4.97 | 3.01 | 3.22 | 37.985 | 189944 | 29.58 | 100 | 3.36 | 3.46 | 4.8 | 4.86 | 4.95 | 4.83 | 4.83 | 4.81 | 4.79 | 4.69 | 3.58 | 3.34 | 38.004 | 189736 | 29.54 | 100 | 3.3 | 3.3 | 4.76 | 4.41 | 4.82 | 4.56 | 4.75 | 4.68 | 4.89 | 4.76 | 3.5 | 3.29 | 191.8638 | 1
2025-11-27 07:41 | 1179299 | 150 | 191 | 1179299 | 195 | 393 | 786 | 31.0561 | 27.304 | 4912829 | 275 | 3715130 | 84 | 18400 | 0 | 28.737 | 188697 | 22.08 | 100 | 3.61 | 3.59 | 3.44 | 3.43 | 3.49 | 3.54 | 3.46 | 3.42 | 3.49 | 1.73 | 3.65 | 3.4 | 18.522 | 186955 | 16.91 | 100 | 1.86 | 1.63 | 1.64 | 1.63 | 1.67 | 1.68 | 1.66 | 1.7 | 1.64 | 1.7 | 3.57 | 3.35 | 20.608 | 186516 | 17.51 | 100 | 1.78 | 1.71 | 1.57 | 1.66 | 1.63 | 1.72 | 1.71 | 1.68 | 3.46 | 3.39 | 3.62 | 3.51 | 39.75 | 191921 | 30.91 | 100 | 3.54 | 3.52 | 4.98 | 5.06 | 5.05 | 5.09 | 5.15 | 5.08 | 4.93 | 5 | 3.46 | 3.65 | 39.996 | 189944 | 30.27 | 100 | 4.04 | 4.1 | 4.82 | 4.89 | 4.98 | 4.87 | 4.86 | 4.85 | 4.82 | 4.73 | 4.25 | 4 | 39.984 | 189737 | 30.23 | 100 | 3.95 | 3.92 | 4.81 | 4.45 | 4.87 | 4.59 | 4.8 | 4.73 | 4.94 | 4.81 | 4.15 | 3.93 | 195.0276 | 1
2025-11-27 07:42 | 1179302 | 153 | 205 | 1179303 | 206 | 398 | 796 | 31.2442 | 27.2005 | 4912834 | 357 | 3715132 | 152 | 18400 | 0 | 29.92 | 188698 | 22.51 | 100 | 3.59 | 3.61 | 3.52 | 3.52 | 3.5 | 3.59 | 3.5 | 3.47 | 3.55 | 3.26 | 3.68 | 3.44 | 18.712 | 186955 | 17.19 | 100 | 1.85 | 1.63 | 1.63 | 1.64 | 1.69 | 1.71 | 1.69 | 1.71 | 1.69 | 1.71 | 3.6 | 3.38 | 20.82 | 186517 | 17.87 | 100 | 1.8 | 1.72 | 1.71 | 1.65 | 1.7 | 1.74 | 1.7 | 1.73 | 3.43 | 3.41 | 3.62 | 3.51 | 43.659 | 191922 | 31.62 | 100 | 5.24 | 5.19 | 5.11 | 5.11 | 5.23 | 5.18 | 5.17 | 5.13 | 5.1 | 5.12 | 5.34 | 5.33 | 42.254 | 189945 | 30.92 | 100 | 5 | 5.08 | 4.95 | 5.06 | 5.04 | 4.89 | 4.91 | 4.9 | 4.88 | 4.84 | 5.23 | 4.94 | 42.272 | 189737 | 30.88 | 100 | 4.97 | 4.84 | 4.9 | 4.65 | 4.9 | 4.69 | 4.9 | 4.83 | 4.95 | 4.9 | 5.02 | 4.72 | 209.46 | 1
2025-11-27 07:43 | 1179306 | 153 | 213 | 1179306 | 214 | 404 | 808 | 31.3947 | 27.3134 | 4912840 | 345 | 3715134 | 132 | 18400 | 0 | 30.541 | 188698 | 23.05 | 100 | 3.68 | 3.69 | 3.54 | 3.58 | 3.61 | 3.65 | 3.57 | 3.53 | 3.62 | 3.29 | 3.73 | 3.5 | 21.64 | 186955 | 17.53 | 100 | 3.47 | 3.22 | 2.99 | 1.65 | 1.7 | 1.74 | 1.73 | 1.72 | 1.73 | 1.71 | 3.7 | 3.49 | 22.605 | 186517 | 18.2 | 100 | 3.01 | 2.96 | 1.74 | 1.67 | 1.7 | 1.69 | 1.74 | 1.74 | 3.56 | 3.46 | 3.73 | 3.61 | 44.412 | 191922 | 32.39 | 100 | 5.38 | 5.31 | 5.18 | 5.17 | 5.33 | 5.29 | 5.3 | 5.21 | 5.14 | 5.2 | 5.43 | 5.42 | 43.065 | 189946 | 31.63 | 100 | 5.1 | 5.17 | 5.03 | 5.15 | 5.15 | 5 | 5 | 4.98 | 4.97 | 4.93 | 5.32 | 5.05 | 42.949 | 189738 | 31.67 | 100 | 5.06 | 4.93 | 4.98 | 4.73 | 4.99 | 4.69 | 4.98 | 4.92 | 5.05 | 4.93 | 5.04 | 4.77 | 217.7482 | 1
2025-11-27 07:44 | 1179310 | 160 | 221 | 1179310 | 221 | 404 | 808 | 31.5263 | 27.351 | 4912846 | 312 | 3715136 | 91 | 18400 | 0 | 30.67 | 188699 | 23.56 | 100 | 3.68 | 3.7 | 3.59 | 3.59 | 3.62 | 3.63 | 3.58 | 3.51 | 3.55 | 3.27 | 3.79 | 3.55 | 27.239 | 186956 | 17.92 | 100 | 3.57 | 3.29 | 3.36 | 2.95 | 3.38 | 2.77 | 3.25 | 1.77 | 3.27 | 3.19 | 3.71 | 3.49 | 24.066 | 186517 | 18.59 | 100 | 3.48 | 3.46 | 3.31 | 1.73 | 1.72 | 1.73 | 1.75 | 1.75 | 3.55 | 3.52 | 3.69 | 3.58 | 44.178 | 191923 | 33.13 | 100 | 5.37 | 5.29 | 5.18 | 5.13 | 5.3 | 5.22 | 5.24 | 5.19 | 5.18 | 5.19 | 5.42 | 5.4 | 42.942 | 189946 | 32.35 | 100 | 5.07 | 5.11 | 5.02 | 5.15 | 5.14 | 4.96 | 4.96 | 4.96 | 4.93 | 4.94 | 5.35 | 5.08 | 42.945 | 189739 | 32.35 | 100 | 5.05 | 4.93 | 4.99 | 4.72 | 5.03 | 4.77 | 4.89 | 4.83 | 5.07 | 4.93 | 5.03 | 4.76 | 226.0302 | 1
2025-11-27 07:45 | 1179313 | 164 | 224 | 1179313 | 224 | 402 | 804 | 31.6768 | 27.5767 | 4912851 | 315 | 3715138 | 91 | 18400 | 0 | 30.611 | 188699 | 24.07 | 100 | 3.64 | 3.67 | 3.58 | 3.5 | 3.64 | 3.65 | 3.56 | 3.57 | 3.6 | 3.34 | 3.76 | 3.52 | 28.543 | 186956 | 18.38 | 100 | 3.6 | 3.31 | 3.32 | 3.33 | 3.45 | 3.39 | 3.38 | 3.06 | 3.42 | 3.34 | 3.7 | 3.48 | 27.152 | 186518 | 18.99 | 100 | 3.48 | 3.46 | 3.48 | 3.34 | 1.74 | 1.76 | 3.42 | 3.35 | 3.58 | 3.51 | 3.73 | 3.63 | 43.798 | 191924 | 33.86 | 100 | 5.24 | 5.2 | 5.14 | 5.1 | 5.24 | 5.21 | 5.22 | 5.14 | 5.06 | 5.14 | 5.31 | 5.34 | 42.695 | 189947 | 33.06 | 100 | 5.05 | 5.11 | 4.98 | 5.1 | 5.1 | 4.95 | 4.94 | 4.97 | 4.92 | 4.89 | 5.26 | 5 | 42.808 | 189739 | 33.02 | 100 | 5 | 4.9 | 4.95 | 4.72 | 5 | 4.75 | 4.94 | 4.87 | 5.09 | 4.98 | 5.08 | 4.78 | 229.2188 | 1
2025-11-27 07:46 | 1179317 | 164 | 223 | 1179317 | 223 | 398 | 796 | 31.8461 | 27.6237 | 4912856 | 319 | 3715139 | 96 | 18400 | 0 | 30.44 | 188700 | 24.57 | 100 | 3.68 | 3.67 | 3.59 | 3.51 | 3.63 | 3.62 | 3.54 | 3.53 | 3.61 | 3.22 | 3.72 | 3.49 | 28.792 | 186957 | 18.86 | 100 | 3.58 | 3.3 | 3.39 | 3.29 | 3.4 | 3.42 | 3.44 | 3.42 | 3.38 | 3.36 | 3.66 | 3.45 | 27.618 | 186518 | 19.5 | 100 | 3.48 | 3.44 | 3.44 | 3.32 | 2.58 | 1.79 | 3.41 | 3.37 | 3.57 | 3.42 | 3.72 | 3.61 | 43.292 | 191925 | 34.59 | 100 | 5.26 | 5.18 | 5.09 | 5.02 | 5.19 | 5.08 | 5.16 | 5.09 | 5.07 | 5.1 | 5.28 | 5.25 | 42.229 | 189948 | 33.77 | 100 | 4.97 | 5.01 | 4.99 | 5.05 | 5.05 | 4.87 | 4.86 | 4.93 | 4.83 | 4.87 | 5.29 | 5.02 | 42.203 | 189740 | 33.73 | 100 | 4.9 | 4.8 | 4.91 | 4.65 | 4.95 | 4.74 | 4.94 | 4.76 | 5.03 | 4.87 | 4.93 | 4.69 | 228.3304 | 1
2025-11-27 07:47 | 1179321 | 171 | 223 | 1179321 | 223 | 393 | 786 | 31.9871 | 27.7083 | 4912862 | 286 | 3715141 | 63 | 18400 | 0 | 30.276 | 188700 | 25.08 | 100 | 3.67 | 3.66 | 3.57 | 3.5 | 3.61 | 3.6 | 3.52 | 3.51 | 3.52 | 3.31 | 3.72 | 3.47 | 28.783 | 186957 | 19.37 | 100 | 3.57 | 3.28 | 3.33 | 3.28 | 3.42 | 3.4 | 3.42 | 3.41 | 3.4 | 3.34 | 3.65 | 3.44 | 28.908 | 186519 | 19.97 | 100 | 3.46 | 3.41 | 3.45 | 3.33 | 3.37 | 3.38 | 3.41 | 3.37 | 3.54 | 3.48 | 3.69 | 3.58 | 42.854 | 191925 | 35.31 | 100 | 5.08 | 5.05 | 5.05 | 4.96 | 5.14 | 5.06 | 5.12 | 5.08 | 4.95 | 5.04 | 5.23 | 5.24 | 41.716 | 189949 | 34.55 | 100 | 4.98 | 5.03 | 4.92 | 4.92 | 4.99 | 4.92 | 4.92 | 4.83 | 4.87 | 4.67 | 5.21 | 4.95 | 41.801 | 189741 | 34.43 | 100 | 4.89 | 4.78 | 4.84 | 4.64 | 4.89 | 4.69 | 4.89 | 4.78 | 4.97 | 4.87 | 5.02 | 4.69 | 228.4429 | 1
2025-11-27 07:48 | 1179324 | 175 | 219 | 1179325 | 219 | 390 | 780 | 32.1 | 27.5861 | 4912866 | 278 | 3715142 | 59 | 18400 | 0 | 30.202 | 188701 | 25.59 | 100 | 3.7 | 3.62 | 3.52 | 3.52 | 3.57 | 3.59 | 3.5 | 3.5 | 3.5 | 3.27 | 3.73 | 3.49 | 28.845 | 186958 | 19.82 | 100 | 3.56 | 3.27 | 3.28 | 3.27 | 3.37 | 3.38 | 3.38 | 3.34 | 3.33 | 3.33 | 3.63 | 3.42 | 28.93 | 186519 | 20.46 | 100 | 3.46 | 3.44 | 3.41 | 3.3 | 3.32 | 3.36 | 3.34 | 3.34 | 3.51 | 3.45 | 3.62 | 3.51 | 40.998 | 191926 | 36 | 100 | 4.35 | 4.34 | 4.99 | 4.97 | 5.08 | 5.04 | 5.05 | 4.97 | 5 | 4.96 | 4.35 | 4.41 | 40.984 | 189949 | 35.2 | 100 | 4.77 | 4.82 | 4.8 | 4.93 | 4.93 | 4.83 | 4.82 | 4.81 | 4.84 | 4.71 | 4.94 | 4.69 | 40.999 | 189741 | 35.12 | 100 | 4.71 | 4.61 | 4.69 | 4.53 | 4.76 | 4.62 | 4.77 | 4.75 | 4.83 | 4.83 | 4.87 | 4.57 | 224.4338 | 1
2025-11-27 07:49 | 1179328 | 175 | 220 | 1179328 | 221 | 390 | 780 | 32.194 | 27.7742 | 4912871 | 282 | 3715143 | 62 | 18400 | 0 | 30.353 | 188701 | 26.09 | 100 | 3.72 | 3.64 | 3.53 | 3.54 | 3.59 | 3.63 | 3.48 | 3.51 | 3.58 | 3.28 | 3.75 | 3.51 | 29.024 | 186958 | 20.33 | 100 | 3.56 | 3.26 | 3.36 | 3.29 | 3.39 | 3.4 | 3.42 | 3.42 | 3.38 | 3.39 | 3.65 | 3.43 | 29.04 | 186520 | 20.94 | 100 | 3.46 | 3.41 | 3.43 | 3.36 | 3.37 | 3.34 | 3.35 | 3.29 | 3.51 | 3.44 | 3.67 | 3.54 | 40.994 | 191927 | 36.65 | 100 | 4.33 | 4.33 | 4.96 | 4.96 | 5.09 | 5.06 | 5.06 | 4.98 | 5.01 | 4.98 | 4.31 | 4.39 | 40.988 | 189950 | 35.92 | 100 | 4.76 | 4.81 | 4.8 | 4.94 | 4.93 | 4.84 | 4.83 | 4.82 | 4.85 | 4.72 | 4.93 | 4.67 | 40.991 | 189742 | 35.84 | 100 | 4.67 | 4.58 | 4.68 | 4.54 | 4.77 | 4.63 | 4.77 | 4.76 | 4.83 | 4.84 | 4.81 | 4.51 | 225.5327 | 1
2025-11-27 07:50 | 1179332 | 182 | 223 | 1179332 | 221 | 397 | 794 | 32.3351 | 27.6143 | 4912876 | 282 | 3715144 | 59 | 18400 | 0 | 30.81 | 188702 | 26.63 | 100 | 3.78 | 3.71 | 3.63 | 3.59 | 3.64 | 3.62 | 3.6 | 3.57 | 3.61 | 3.34 | 3.77 | 3.53 | 29.435 | 186959 | 20.76 | 100 | 3.59 | 3.33 | 3.41 | 3.34 | 3.48 | 3.46 | 3.44 | 3.38 | 3.39 | 3.41 | 3.71 | 3.48 | 29.334 | 186520 | 21.4 | 100 | 3.49 | 3.45 | 3.42 | 3.34 | 3.41 | 3.43 | 3.38 | 3.38 | 3.54 | 3.47 | 3.71 | 3.6 | 41.527 | 191927 | 37.33 | 100 | 4.46 | 4.45 | 5.07 | 5.05 | 5.15 | 5.12 | 5.12 | 5.04 | 5.07 | 5.04 | 4.44 | 4.51 | 41.794 | 189951 | 36.53 | 100 | 5.07 | 5.07 | 4.97 | 5 | 5.01 | 4.96 | 4.97 | 4.89 | 4.91 | 4.78 | 4.69 | 4.44 | 41.623 | 189743 | 36.53 | 100 | 4.88 | 4.77 | 4.88 | 4.6 | 4.91 | 4.7 | 4.82 | 4.67 | 4.98 | 4.78 | 5.06 | 4.76 | 228.7209 | 1
2025-11-27 07:51 | 1179335 | 186 | 222 | 1179336 | 222 | 398 | 796 | 32.4103 | 27.7648 | 4912880 | 280 | 3715145 | 58 | 18400 | 0 | 31.063 | 188702 | 27.11 | 100 | 3.8 | 3.73 | 3.66 | 3.62 | 3.7 | 3.7 | 3.62 | 3.59 | 3.63 | 3.34 | 3.82 | 3.58 | 29.767 | 186959 | 21.28 | 100 | 3.57 | 3.31 | 3.43 | 3.26 | 3.51 | 3.43 | 3.47 | 3.42 | 3.39 | 3.4 | 3.68 | 3.44 | 29.701 | 186521 | 21.89 | 100 | 3.54 | 3.5 | 3.46 | 3.43 | 3.45 | 3.37 | 3.42 | 3.41 | 3.55 | 3.45 | 3.73 | 3.61 | 40.984 | 191928 | 38.06 | 100 | 4.08 | 4.08 | 5.1 | 5.08 | 5.18 | 5.15 | 5.15 | 5.06 | 5.11 | 5.05 | 4.04 | 4.16 | 41.012 | 189951 | 37.26 | 100 | 4.4 | 4.47 | 5 | 5.03 | 5.04 | 4.99 | 4.99 | 4.9 | 4.92 | 4.79 | 4.66 | 4.41 | 40.993 | 189744 | 37.21 | 100 | 4.3 | 4.26 | 4.89 | 4.66 | 4.94 | 4.72 | 4.91 | 4.79 | 5.01 | 4.88 | 4.51 | 4.27 | 227.7552 | 1
2025-11-27 07:52 | 1179339 | 186 | 221 | 1179339 | 221 | 405 | 810 | 32.5232 | 27.8964 | 4912885 | 274 | 3715146 | 53 | 18400 | 0 | 31.576 | 188703 | 27.66 | 100 | 3.91 | 3.82 | 3.75 | 3.65 | 3.7 | 3.75 | 3.7 | 3.66 | 3.69 | 3.45 | 3.86 | 3.61 | 30.649 | 186960 | 21.81 | 100 | 3.63 | 3.37 | 3.47 | 3.38 | 3.53 | 3.54 | 3.51 | 3.53 | 3.51 | 3.48 | 3.81 | 3.6 | 30.521 | 186521 | 22.39 | 100 | 3.59 | 3.54 | 3.54 | 3.45 | 3.39 | 3.52 | 3.54 | 3.53 | 3.67 | 3.6 | 3.75 | 3.64 | 39.909 | 191929 | 38.69 | 100 | 3.43 | 3.45 | 5.18 | 5.16 | 5.26 | 5.22 | 5.23 | 5.14 | 5.19 | 5.14 | 3.37 | 3.56 | 39.487 | 189952 | 37.93 | 100 | 3.52 | 3.64 | 5.07 | 5.12 | 5.11 | 5.07 | 5.08 | 4.99 | 5.01 | 4.88 | 3.75 | 3.51 | 39.981 | 189744 | 37.88 | 100 | 3.69 | 3.72 | 4.98 | 4.75 | 5.03 | 4.8 | 4.99 | 4.89 | 5.09 | 4.96 | 3.91 | 3.71 | 226.8188 | 1
2025-11-27 07:53 | 1179343 | 193 | 220 | 1179343 | 220 | 411 | 822 | 32.6078 | 27.8776 | 4912889 | 270 | 3715146 | 50 | 18400 | 0 | 31.992 | 188703 | 28.19 | 100 | 3.9 | 3.83 | 3.77 | 3.76 | 3.79 | 3.76 | 3.75 | 3.72 | 3.8 | 3.52 | 3.95 | 3.7 | 31.111 | 186960 | 22.3 | 100 | 3.72 | 3.48 | 3.53 | 3.47 | 3.6 | 3.6 | 3.57 | 3.61 | 3.58 | 3.58 | 3.87 | 3.66 | 31.067 | 186522 | 22.9 | 100 | 3.66 | 3.61 | 3.59 | 3.52 | 3.45 | 3.56 | 3.6 | 3.57 | 3.73 | 3.63 | 3.86 | 3.74 | 38.986 | 191929 | 39.38 | 100 | 3.03 | 3.04 | 5.25 | 5.25 | 5.34 | 5.32 | 5.31 | 5.23 | 5.28 | 5.22 | 2.95 | 3.17 | 38.988 | 189953 | 38.62 | 100 | 3.27 | 3.42 | 5.15 | 5.21 | 5.19 | 5.15 | 5.17 | 5.07 | 5.09 | 4.96 | 3.5 | 3.28 | 39.003 | 189745 | 38.57 | 100 | 3.16 | 3.24 | 5.04 | 4.81 | 5.09 | 4.87 | 5.06 | 4.96 | 5.17 | 5.04 | 3.39 | 3.2 | 225.8594 | 1
2025-11-27 07:54 | 1179347 | 197 | 230 | 1179347 | 231 | 416 | 832 | 32.7018 | 27.9058 | 4912894 | 294 | 3715147 | 64 | 18400 | 0 | 32.471 | 188704 | 28.73 | 100 | 3.93 | 3.86 | 3.79 | 3.79 | 3.81 | 3.86 | 3.77 | 3.76 | 3.81 | 3.52 | 4.01 | 3.75 | 31.594 | 186961 | 22.85 | 100 | 3.77 | 3.52 | 3.59 | 3.52 | 3.65 | 3.61 | 3.58 | 3.68 | 3.66 | 3.64 | 3.9 | 3.66 | 31.599 | 186522 | 23.42 | 100 | 3.74 | 3.71 | 3.66 | 3.62 | 3.61 | 3.65 | 3.59 | 3.63 | 3.77 | 3.72 | 3.87 | 3.77 | 41.593 | 191930 | 40.04 | 100 | 3.76 | 3.79 | 5.32 | 5.31 | 5.41 | 5.38 | 5.38 | 5.29 | 5.34 | 5.29 | 3.71 | 3.88 | 41.359 | 189953 | 39.24 | 100 | 3.96 | 4.09 | 5.22 | 5.27 | 5.26 | 5.22 | 5.24 | 5.13 | 5.16 | 5.03 | 4.2 | 3.95 | 42.01 | 189746 | 39.19 | 100 | 4.14 | 4.16 | 5.13 | 4.89 | 5.18 | 4.94 | 5.14 | 5.02 | 5.25 | 5.12 | 4.37 | 4.15 | 236.2034 | 1
2025-11-27 07:55 | 1179350 | 197 | 232 | 1179351 | 231 | 419 | 838 | 32.7677 | 27.9622 | 4912898 | 288 | 3715148 | 56 | 18400 | 0 | 32.786 | 188704 | 29.24 | 100 | 4.02 | 3.97 | 3.87 | 3.84 | 3.88 | 3.89 | 3.84 | 3.8 | 3.84 | 3.49 | 4.01 | 3.75 | 31.969 | 186961 | 23.35 | 100 | 3.79 | 3.56 | 3.66 | 3.56 | 3.73 | 3.66 | 3.7 | 3.67 | 3.71 | 3.67 | 3.95 | 3.73 | 31.943 | 186523 | 23.98 | 100 | 3.74 | 3.7 | 3.67 | 3.64 | 3.67 | 3.67 | 3.69 | 3.65 | 3.84 | 3.73 | 3.96 | 3.84 | 41.981 | 191931 | 40.76 | 100 | 3.86 | 3.89 | 5.37 | 5.35 | 5.45 | 5.43 | 5.42 | 5.33 | 5.38 | 5.33 | 3.82 | 3.98 | 41.983 | 189954 | 39.96 | 100 | 4.16 | 4.27 | 5.26 | 5.3 | 5.29 | 5.25 | 5.27 | 5.17 | 5.19 | 5.06 | 4.4 | 4.14 | 41.984 | 189746 | 39.87 | 100 | 4.03 | 4.05 | 5.16 | 4.92 | 5.22 | 4.98 | 5.18 | 5.07 | 5.29 | 5.16 | 4.24 | 4.07 | 238.3124 | 1
2025-11-27 07:56 | 1179354 | 204 | 230 | 1179354 | 230 | 426 | 852 | 32.8429 | 27.9904 | 4912903 | 284 | 3715149 | 54 | 18400 | 0 | 33.296 | 188705 | 29.82 | 100 | 4.08 | 4.02 | 3.94 | 3.92 | 3.95 | 3.93 | 3.93 | 3.88 | 3.95 | 3.54 | 4.1 | 3.84 | 32.401 | 186962 | 23.91 | 100 | 3.89 | 3.62 | 3.74 | 3.63 | 3.79 | 3.75 | 3.75 | 3.76 | 3.72 | 3.69 | 4.02 | 3.8 | 32.402 | 186523 | 24.52 | 100 | 3.81 | 3.77 | 3.79 | 3.7 | 3.69 | 3.72 | 3.75 | 3.7 | 3.89 | 3.81 | 4.01 | 3.89 | 40.986 | 191931 | 41.45 | 100 | 3.3 | 3.33 | 5.48 | 5.47 | 5.56 | 5.53 | 5.52 | 5.42 | 5.49 | 5.42 | 3.23 | 3.45 | 40.996 | 189955 | 40.68 | 100 | 3.56 | 3.72 | 5.37 | 5.42 | 5.4 | 5.37 | 5.37 | 5.27 | 5.29 | 5.15 | 3.82 | 3.56 | 40.983 | 189747 | 40.6 | 100 | 3.48 | 3.55 | 5.25 | 5.02 | 5.3 | 5.06 | 5.27 | 5.15 | 5.38 | 5.24 | 3.69 | 3.54 | 236.3202 | 1
2025-11-27 07:57 | 1179358 | 208 | 235 | 1179358 | 232 | 435 | 870 | 32.9275 | 27.9622 | 4912908 | 281 | 3715150 | 46 | 18400 | 0 | 34.18 | 188706 | 30.35 | 100 | 4.2 | 4.13 | 3.98 | 3.99 | 4 | 4.07 | 3.99 | 3.96 | 4 | 3.7 | 4.23 | 3.97 | 33.029 | 186962 | 24.46 | 100 | 3.97 | 3.7 | 3.77 | 3.7 | 3.86 | 3.83 | 3.85 | 3.77 | 3.84 | 3.8 | 4.1 | 3.88 | 32.948 | 186524 | 25.06 | 100 | 3.88 | 3.83 | 3.81 | 3.77 | 3.8 | 3.81 | 3.82 | 3.74 | 3.92 | 3.82 | 4.09 | 3.95 | 41 | 191932 | 42.13 | 100 | 3.07 | 3.12 | 5.58 | 5.57 | 5.66 | 5.64 | 5.6 | 5.52 | 5.59 | 5.51 | 3 | 3.25 | 41.995 | 189955 | 41.29 | 100 | 3.72 | 3.88 | 5.47 | 5.51 | 5.49 | 5.47 | 5.48 | 5.36 | 5.39 | 5.24 | 3.98 | 3.72 | 40.969 | 189748 | 41.33 | 100 | 3.25 | 3.37 | 5.34 | 5.11 | 5.4 | 5.16 | 5.36 | 5.25 | 5.48 | 5.33 | 3.46 | 3.34 | 241.5292 | 1
2025-11-27 07:58 | 1179362 | 208 | 228 | 1179362 | 228 | 440 | 880 | 32.984 | 27.9246 | 4912913 | 270 | 3715151 | 42 | 18400 | 0 | 34.721 | 188706 | 30.92 | 100 | 4.23 | 4.17 | 4.09 | 4.01 | 4.11 | 4.13 | 4.03 | 4.03 | 4.09 | 3.75 | 4.25 | 3.99 | 33.805 | 186963 | 25.04 | 100 | 4.04 | 3.76 | 3.89 | 3.77 | 3.94 | 3.91 | 3.92 | 3.94 | 3.89 | 3.81 | 4.17 | 3.93 | 33.564 | 186524 | 25.61 | 100 | 3.96 | 3.91 | 3.89 | 3.81 | 3.89 | 3.86 | 3.89 | 3.88 | 3.99 | 3.91 | 4.16 | 4.02 | 40.023 | 191933 | 42.8 | 100 | 2.66 | 2.7 | 5.27 | 5.22 | 5.26 | 5.26 | 5.26 | 5.31 | 5.3 | 5.26 | 2.56 | 2.86 | 39.016 | 189956 | 42 | 100 | 2.61 | 2.82 | 5.37 | 5.34 | 5.33 | 5.34 | 5.33 | 5.33 | 5.33 | 5.31 | 2.88 | 2.64 | 38.959 | 189748 | 42 | 100 | 2.54 | 2.71 | 5.23 | 5.1 | 5.24 | 5.14 | 5.16 | 5.27 | 5.27 | 5.23 | 2.74 | 2.66 | 234.3811 | 1
2025-11-27 07:59 | 1179366 | 216 | 229 | 1179366 | 232 | 446 | 892 | 33.0498 | 27.9434 | 4912917 | 274 | 3715151 | 45 | 18400 | 0 | 35.145 | 188707 | 31.5 | 100 | 4.26 | 4.21 | 4.14 | 4.06 | 4.16 | 4.18 | 4.11 | 4.04 | 4.15 | 3.84 | 4.3 | 4.04 | 34.112 | 186963 | 25.54 | 100 | 4.09 | 3.79 | 3.88 | 3.81 | 3.93 | 3.93 | 3.97 | 3.98 | 3.95 | 3.93 | 4.16 | 3.89 | 34.148 | 186525 | 26.21 | 100 | 4.01 | 3.95 | 3.97 | 3.9 | 3.89 | 3.93 | 3.94 | 3.9 | 4.09 | 3.99 | 4.25 | 4.1 | 39.012 | 191933 | 43.46 | 100 | 2.65 | 2.7 | 5.26 | 5.22 | 5.25 | 5.25 | 5.25 | 5.29 | 5.29 | 5.26 | 2.55 | 2.86 | 38.973 | 189957 | 42.66 | 100 | 2.59 | 2.81 | 5.34 | 5.31 | 5.31 | 5.32 | 5.3 | 5.31 | 5.3 | 5.32 | 2.86 | 2.62 | 39.009 | 189749 | 42.61 | 100 | 2.53 | 2.7 | 5.21 | 5.07 | 5.23 | 5.12 | 5.16 | 5.27 | 5.25 | 5.21 | 2.73 | 2.65 | 235.4634 | 1
2025-11-27 08:00 | 1179370 | 220 | 233 | 1179370 | 230 | 448 | 896 | 33.0968 | 27.8682 | 4912922 | 269 | 3715152 | 36 | 18400 | 0 | 35.222 | 188707 | 32.11 | 100 | 4.26 | 4.21 | 4.17 | 4.08 | 4.19 | 4.18 | 4.1 | 4.1 | 4.13 | 3.84 | 4.34 | 4.09 | 34.427 | 186964 | 26.14 | 100 | 4.1 | 3.81 | 3.95 | 3.85 | 4.04 | 3.98 | 4 | 4.01 | 3.95 | 3.96 | 4.23 | 3.97 | 34.434 | 186526 | 26.74 | 100 | 4.04 | 3.99 | 4.01 | 3.92 | 3.97 | 3.97 | 3.98 | 3.97 | 4.13 | 4.04 | 4.24 | 4.12 | 39.999 | 191934 | 44.11 | 100 | 2.75 | 2.82 | 5.47 | 5.42 | 5.44 | 5.45 | 5.46 | 5.5 | 5.49 | 5.45 | 2.65 | 2.97 | 40.017 | 189957 | 43.31 | 100 | 2.72 | 2.96 | 5.61 | 5.59 | 5.57 | 5.59 | 5.59 | 5.5 | 5.51 | 5.37 | 3 | 2.73 | 39.964 | 189750 | 43.27 | 100 | 2.64 | 2.83 | 5.46 | 5.26 | 5.45 | 5.3 | 5.41 | 5.4 | 5.48 | 5.46 | 2.87 | 2.76 | 239.6158 | 1
2025-11-27 08:01 | 1179374 | 220 | 230 | 1179374 | 230 | 450 | 900 | 33.1438 | 27.7836 | 4912926 | 267 | 3715152 | 37 | 18400 | 0 | 35.372 | 188708 | 32.7 | 100 | 4.3 | 4.25 | 4.23 | 4.15 | 4.18 | 4.29 | 4.12 | 4.13 | 4.22 | 3.8 | 4.36 | 4.11 | 34.525 | 186965 | 26.72 | 100 | 4.12 | 3.86 | 4 | 3.86 | 4.06 | 3.98 | 4.02 | 4.04 | 4.04 | 3.94 | 4.25 | 4 | 34.506 | 186526 | 27.35 | 100 | 4.03 | 3.97 | 4.02 | 3.95 | 3.92 | 3.99 | 4.01 | 3.97 | 4.16 | 4.06 | 4.27 | 4.14 | 39.026 | 191935 | 44.79 | 100 | 2.64 | 2.72 | 5.26 | 5.22 | 5.26 | 5.26 | 5.26 | 5.31 | 5.3 | 5.27 | 2.56 | 2.86 | 38.958 | 189958 | 43.99 | 100 | 2.6 | 2.83 | 5.36 | 5.34 | 5.33 | 5.34 | 5.33 | 5.33 | 5.33 | 5.36 | 2.88 | 2.63 | 38.959 | 189750 | 43.91 | 100 | 2.52 | 2.71 | 5.21 | 5.08 | 5.23 | 5.11 | 5.16 | 5.26 | 5.25 | 5.22 | 2.74 | 2.64 | 236.5696 | 1
2025-11-27 08:02 | 1179377 | 228 | 234 | 1179378 | 234 | 451 | 902 | 33.172 | 27.8494 | 4912930 | 272 | 3715153 | 38 | 18400 | 0 | 35.618 | 188708 | 33.29 | 100 | 4.39 | 4.33 | 4.26 | 4.13 | 4.23 | 4.25 | 4.15 | 4.11 | 4.16 | 3.82 | 4.42 | 4.16 | 34.876 | 186965 | 27.3 | 100 | 4.17 | 3.88 | 4.04 | 3.9 | 4.09 | 4.03 | 4.01 | 4.07 | 4.09 | 4.01 | 4.28 | 4.03 | 34.876 | 186527 | 27.89 | 100 | 4.13 | 4.09 | 4.08 | 3.98 | 4.03 | 4.03 | 4.04 | 4.02 | 4.19 | 4.1 | 4.3 | 4.17 | 39.561 | 191935 | 45.4 | 100 | 2.69 | 2.76 | 5.35 | 5.3 | 5.34 | 5.34 | 5.34 | 5.38 | 5.37 | 5.34 | 2.6 | 2.91 | 40 | 189959 | 44.6 | 100 | 2.7 | 2.95 | 5.58 | 5.55 | 5.53 | 5.55 | 5.55 | 5.52 | 5.53 | 5.41 | 2.98 | 2.74 | 39.979 | 189751 | 44.56 | 100 | 2.61 | 2.81 | 5.4 | 5.26 | 5.41 | 5.3 | 5.36 | 5.44 | 5.43 | 5.4 | 2.85 | 2.73 | 240.7077 | 1
2025-11-27 08:03 | 1179381 | 231 | 230 | 1179382 | 230 | 447 | 894 | 33.2096 | 27.7836 | 4912935 | 268 | 3715154 | 38 | 18400 | 0 | 35.34 | 188709 | 33.91 | 100 | 4.27 | 4.21 | 4.21 | 4.09 | 4.2 | 4.23 | 4.14 | 4.1 | 4.14 | 3.8 | 4.31 | 4.05 | 34.567 | 186966 | 27.9 | 100 | 4.14 | 3.85 | 3.99 | 3.87 | 4.05 | 3.96 | 4.02 | 4 | 4.04 | 3.97 | 4.24 | 3.99 | 34.604 | 186527 | 28.47 | 100 | 4.09 | 4.05 | 4.01 | 3.94 | 4.02 | 4 | 4 | 3.97 | 4.16 | 4.05 | 4.26 | 4.09 | 38.986 | 191936 | 46.07 | 100 | 2.65 | 2.73 | 5.29 | 5.24 | 5.27 | 5.27 | 5.27 | 5.32 | 5.32 | 5.28 | 2.57 | 2.87 | 39.021 | 189959 | 45.27 | 100 | 2.6 | 2.85 | 5.39 | 5.36 | 5.35 | 5.36 | 5.35 | 5.35 | 5.35 | 5.33 | 2.88 | 2.65 | 39.018 | 189752 | 45.26 | 100 | 2.52 | 2.73 | 5.23 | 5.09 | 5.24 | 5.13 | 5.18 | 5.28 | 5.26 | 5.23 | 2.76 | 2.64 | 236.6242 | 1
2025-11-27 08:04 | 1179385 | 231 | 234 | 1179385 | 234 | 449 | 898 | 33.2096 | 27.7648 | 4912939 | 270 | 3715154 | 36 | 18400 | 0 | 35.726 | 188710 | 34.47 | 100 | 4.39 | 4.31 | 4.22 | 4.18 | 4.24 | 4.32 | 4.19 | 4.16 | 4.19 | 3.87 | 4.39 | 4.13 | 34.842 | 186966 | 28.48 | 100 | 4.23 | 3.92 | 4.03 | 3.93 | 4.09 | 4.02 | 4.04 | 4.03 | 4.06 | 4.03 | 4.25 | 3.99 | 34.865 | 186528 | 29.02 | 100 | 4.12 | 4.08 | 4.05 | 3.96 | 4.06 | 4.02 | 4.02 | 3.94 | 4.2 | 4.07 | 4.34 | 4.19 | 39.998 | 191937 | 46.73 | 100 | 2.75 | 2.83 | 5.49 | 5.43 | 5.46 | 5.47 | 5.47 | 5.51 | 5.5 | 5.47 | 2.67 | 2.97 | 40.018 | 189960 | 45.97 | 100 | 2.74 | 2.99 | 5.58 | 5.62 | 5.59 | 5.59 | 5.6 | 5.48 | 5.5 | 5.35 | 3.02 | 2.8 | 39.995 | 189752 | 45.89 | 100 | 2.64 | 2.84 | 5.46 | 5.24 | 5.47 | 5.29 | 5.42 | 5.38 | 5.48 | 5.46 | 2.89 | 2.75 | 240.7394 | 1
2025-11-27 08:05 | 1179389 | 239 | 233 | 1179389 | 230 | 445 | 890 | 33.2379 | 27.7836 | 4912944 | 266 | 3715155 | 33 | 18400 | 0 | 35.366 | 188710 | 35.07 | 100 | 4.36 | 4.29 | 4.18 | 4.13 | 4.2 | 4.22 | 4.15 | 4.08 | 4.17 | 3.84 | 4.34 | 4.09 | 34.536 | 186967 | 29.03 | 100 | 4.11 | 3.85 | 3.92 | 3.86 | 4.04 | 4 | 4.01 | 4.03 | 4.07 | 3.97 | 4.28 | 4.04 | 34.512 | 186528 | 29.66 | 100 | 4.1 | 4.07 | 4.02 | 3.94 | 4.03 | 4.01 | 4.04 | 3.96 | 4.15 | 4.07 | 4.32 | 4.16 | 39.521 | 191937 | 47.42 | 100 | 2.73 | 2.82 | 5.48 | 5.41 | 5.44 | 5.46 | 5.46 | 5.47 | 5.49 | 5.46 | 2.65 | 2.95 | 39.025 | 189961 | 46.62 | 100 | 2.62 | 2.87 | 5.43 | 5.39 | 5.38 | 5.4 | 5.39 | 5.38 | 5.37 | 5.27 | 2.89 | 2.67 | 39.97 | 189753 | 46.54 | 100 | 2.77 | 2.96 | 5.39 | 5.16 | 5.46 | 5.22 | 5.42 | 5.31 | 5.54 | 5.38 | 3.02 | 2.88 | 239.7344 | 1
2025-11-27 08:06 | 1179393 | 243 | 239 | 1179393 | 239 | 452 | 904 | 33.2849 | 27.9622 | 4912949 | 321 | 3715156 | 82 | 18400 | 0 | 36.171 | 188711 | 35.69 | 100 | 4.4 | 4.34 | 4.26 | 4.2 | 4.26 | 4.33 | 4.26 | 4.2 | 4.3 | 3.93 | 4.41 | 4.14 | 35.289 | 186967 | 29.64 | 100 | 4.22 | 3.93 | 4.09 | 3.94 | 4.07 | 4.07 | 4.04 | 4.13 | 4.14 | 4.08 | 4.31 | 4.04 | 35.227 | 186529 | 30.21 | 100 | 4.17 | 4.13 | 4.13 | 4 | 4.1 | 4.08 | 4.1 | 4.04 | 4.23 | 4.14 | 4.38 | 4.23 | 41.015 | 191938 | 48.08 | 100 | 2.85 | 2.93 | 5.68 | 5.62 | 5.64 | 5.66 | 5.67 | 5.65 | 5.69 | 5.66 | 2.76 | 3.06 | 40.278 | 189961 | 47.27 | 100 | 2.72 | 2.98 | 5.58 | 5.56 | 5.54 | 5.56 | 5.55 | 5.51 | 5.52 | 5.39 | 3 | 2.79 | 40.99 | 189754 | 47.23 | 100 | 2.87 | 3.07 | 5.51 | 5.27 | 5.58 | 5.34 | 5.54 | 5.43 | 5.66 | 5.5 | 3.12 | 2.99 | 245.9484 | 1
2025-11-27 08:07 | 1179397 | 243 | 260 | 1179397 | 258 | 453 | 906 | 33.4165 | 28.0845 | 4912954 | 309 | 3715157 | 49 | 18400 | 0 | 36.199 | 188711 | 36.26 | 100 | 4.45 | 4.39 | 4.31 | 4.23 | 4.34 | 4.38 | 4.24 | 4.21 | 4.24 | 3.92 | 4.43 | 4.12 | 35.378 | 186968 | 30.19 | 100 | 4.22 | 3.93 | 4.09 | 3.96 | 4.13 | 4.09 | 4.1 | 4.15 | 4.1 | 4.06 | 4.32 | 4.07 | 35.248 | 186530 | 30.82 | 100 | 4.17 | 4.14 | 4.13 | 4.05 | 4.11 | 4.08 | 4.07 | 4.06 | 4.23 | 4.14 | 4.4 | 4.24 | 47.852 | 191939 | 48.86 | 100 | 5.51 | 5.51 | 5.82 | 5.64 | 5.91 | 5.72 | 5.87 | 5.9 | 5.76 | 5.78 | 5.48 | 5.54 | 46.999 | 189962 | 48.04 | 100 | 5.38 | 5.48 | 5.71 | 5.76 | 5.74 | 5.69 | 5.54 | 5.56 | 5.59 | 5.44 | 5.63 | 5.36 | 47.434 | 189754 | 47.96 | 100 | 5.12 | 5.11 | 5.56 | 5.31 | 5.63 | 5.37 | 5.58 | 5.54 | 5.7 | 5.62 | 5.36 | 5.14 | 267.6826 | 1
2025-11-27 08:08 | 1179402 | 251 | 259 | 1179402 | 259 | 470 | 940 | 33.5576 | 28.1785 | 4912959 | 310 | 3715157 | 51 | 18400 | 0 | 37.778 | 188712 | 36.91 | 100 | 4.58 | 4.54 | 4.53 | 4.41 | 4.47 | 4.48 | 4.42 | 4.4 | 4.49 | 4.15 | 4.53 | 4.28 | 36.856 | 186969 | 30.82 | 100 | 4.46 | 4.15 | 4.27 | 4.12 | 4.33 | 4.29 | 4.27 | 4.3 | 4.32 | 4.22 | 4.51 | 4.27 | 36.561 | 186530 | 31.38 | 100 | 4.35 | 4.31 | 4.29 | 4.17 | 4.26 | 4.22 | 4.27 | 4.2 | 4.38 | 4.28 | 4.52 | 4.37 | 46.032 | 191940 | 49.59 | 100 | 4.03 | 4.1 | 6.05 | 5.86 | 6.13 | 5.94 | 6.09 | 6.13 | 6 | 6 | 3.98 | 4.2 | 46.023 | 189963 | 48.81 | 100 | 4.28 | 4.49 | 5.93 | 5.98 | 5.98 | 5.92 | 5.75 | 5.77 | 5.79 | 5.62 | 4.55 | 4.35 | 45.995 | 189755 | 48.77 | 100 | 4.13 | 4.25 | 5.76 | 5.52 | 5.84 | 5.58 | 5.79 | 5.75 | 5.91 | 5.84 | 4.39 | 4.22 | 266.7852 | 1
2025-11-27 08:09 | 1179406 | 256 | 262 | 1179406 | 262 | 482 | 964 | 33.7551 | 28.376 | 4912964 | 308 | 3715158 | 46 | 18400 | 0 | 38.774 | 188713 | 37.5 | 100 | 4.77 | 4.71 | 4.61 | 4.56 | 4.64 | 4.6 | 4.53 | 4.5 | 4.57 | 4.17 | 4.73 | 4.48 | 37.601 | 186969 | 31.44 | 100 | 4.5 | 4.2 | 4.4 | 4.27 | 4.44 | 4.36 | 4.39 | 4.42 | 4.41 | 4.38 | 4.61 | 4.36 | 37.594 | 186531 | 32.03 | 100 | 4.45 | 4.41 | 4.38 | 4.31 | 4.4 | 4.37 | 4.34 | 4.36 | 4.48 | 4.42 | 4.65 | 4.51 | 45.997 | 191940 | 50.4 | 100 | 3.83 | 3.9 | 6.18 | 5.98 | 6.26 | 6.07 | 6.22 | 6.27 | 6.12 | 6.13 | 3.76 | 4.01 | 45.985 | 189964 | 49.57 | 100 | 4.09 | 4.32 | 6.06 | 6.12 | 6.1 | 6.05 | 5.86 | 5.87 | 5.91 | 5.73 | 4.36 | 4.08 | 46.045 | 189756 | 49.5 | 100 | 3.97 | 4.11 | 5.87 | 5.63 | 5.94 | 5.67 | 5.89 | 5.86 | 6.03 | 5.96 | 4.14 | 3.97 | 270.0627 | 1
2025-11-27 08:10 | 1179410 | 256 | 267 | 1179411 | 267 | 490 | 980 | 33.9619 | 28.3666 | 4912969 | 312 | 3715159 | 45 | 18400 | 0 | 39.343 | 188713 | 38.15 | 100 | 4.81 | 4.76 | 4.72 | 4.61 | 4.73 | 4.68 | 4.55 | 4.58 | 4.65 | 4.28 | 4.84 | 4.53 | 38.538 | 186970 | 32.04 | 100 | 4.62 | 4.33 | 4.46 | 4.32 | 4.5 | 4.45 | 4.47 | 4.55 | 4.51 | 4.46 | 4.72 | 4.47 | 38.1 | 186531 | 32.62 | 100 | 4.53 | 4.49 | 4.46 | 4.38 | 4.47 | 4.44 | 4.48 | 4.42 | 4.56 | 4.45 | 4.74 | 4.59 | 46.016 | 191941 | 51.17 | 100 | 3.59 | 3.67 | 6.25 | 6.05 | 6.35 | 6.14 | 6.3 | 6.36 | 6.2 | 6.21 | 3.52 | 3.78 | 46.509 | 189964 | 50.34 | 100 | 3.97 | 4.21 | 6.16 | 6.22 | 6.2 | 6.15 | 5.95 | 5.97 | 6.01 | 5.82 | 4.25 | 4.04 | 47.015 | 189757 | 50.31 | 100 | 4.12 | 4.27 | 5.96 | 5.72 | 6.04 | 5.75 | 5.99 | 5.95 | 6.13 | 6.07 | 4.4 | 4.22 | 275.4168 | 1
2025-11-27 08:11 | 1179415 | 264 | 265 | 1179415 | 265 | 492 | 984 | 34.0842 | 28.2914 | 4912975 | 311 | 3715160 | 46 | 18400 | 0 | 39.643 | 188714 | 38.84 | 100 | 4.85 | 4.81 | 4.71 | 4.67 | 4.74 | 4.75 | 4.64 | 4.63 | 4.69 | 4.3 | 4.83 | 4.6 | 38.879 | 186971 | 32.71 | 100 | 4.61 | 4.32 | 4.5 | 4.35 | 4.58 | 4.5 | 4.46 | 4.59 | 4.56 | 4.51 | 4.75 | 4.5 | 38.775 | 186532 | 33.3 | 100 | 4.58 | 4.55 | 4.55 | 4.44 | 4.55 | 4.51 | 4.56 | 4.52 | 4.67 | 4.52 | 4.82 | 4.65 | 45.979 | 191942 | 51.9 | 100 | 3.58 | 3.66 | 6.26 | 6.05 | 6.35 | 6.15 | 6.31 | 6.38 | 6.21 | 6.23 | 3.51 | 3.77 | 46.018 | 189965 | 51.16 | 100 | 3.83 | 4.09 | 6.19 | 6.25 | 6.22 | 6.19 | 5.97 | 6 | 6.03 | 5.85 | 4.11 | 3.92 | 45.965 | 189757 | 51.04 | 100 | 3.59 | 3.78 | 6 | 5.75 | 6.09 | 5.82 | 6.03 | 6 | 6.18 | 6.12 | 3.95 | 3.8 | 273.4714 | 1
2025-11-27 08:12 | 1179419 | 269 | 249 | 1179419 | 252 | 489 | 978 | 34.2253 | 28.4418 | 4912979 | 282 | 3715160 | 33 | 18400 | 0 | 39.141 | 188715 | 39.49 | 100 | 4.81 | 4.74 | 4.63 | 4.64 | 4.76 | 4.62 | 4.61 | 4.58 | 4.68 | 4.37 | 4.79 | 4.54 | 38.422 | 186971 | 33.35 | 100 | 4.58 | 4.3 | 4.44 | 4.34 | 4.51 | 4.41 | 4.44 | 4.58 | 4.58 | 4.45 | 4.74 | 4.48 | 38.506 | 186533 | 33.94 | 100 | 4.57 | 4.54 | 4.54 | 4.38 | 4.44 | 4.51 | 4.52 | 4.48 | 4.63 | 4.54 | 4.76 | 4.62 | 40.985 | 191943 | 52.61 | 100 | 2.77 | 2.87 | 5.54 | 5.49 | 5.53 | 5.53 | 5.53 | 5.57 | 5.57 | 5.54 | 2.69 | 3.01 | 41.982 | 189966 | 51.87 | 100 | 2.78 | 3.09 | 5.8 | 5.77 | 5.76 | 5.77 | 5.77 | 5.76 | 5.76 | 5.77 | 3.05 | 2.9 | 40.971 | 189758 | 51.75 | 100 | 2.61 | 2.87 | 5.46 | 5.33 | 5.48 | 5.36 | 5.41 | 5.52 | 5.51 | 5.47 | 2.88 | 2.76 | 257.0875 | 1
2025-11-27 08:13 | 1179423 | 269 | 248 | 1179423 | 248 | 498 | 996 | 34.3945 | 28.4701 | 4912984 | 276 | 3715161 | 28 | 18400 | 0 | 40.041 | 188715 | 40.15 | 40 | 4.81 | 4.79 | 4.79 | 4.75 | 4.82 | 4.84 | 4.75 | 4.69 | 4.76 | 4.44 | 4.83 | 4.57 | 39.254 | 186972 | 34 | 40 | 4.74 | 4.45 | 4.59 | 4.44 | 4.56 | 4.61 | 4.54 | 4.67 | 4.67 | 4.59 | 4.84 | 4.53 | 39.163 | 186533 | 34.58 | 40 | 4.65 | 4.62 | 4.63 | 4.52 | 4.59 | 4.6 | 4.61 | 4.48 | 4.73 | 4.64 | 4.89 | 4.72 | 40.041 | 191943 | 53.34 | 40 | 2.67 | 2.77 | 5.32 | 5.29 | 5.33 | 5.32 | 5.31 | 5.37 | 5.37 | 5.34 | 2.59 | 2.89 | 40.017 | 189967 | 52.55 | 40 | 2.57 | 2.89 | 5.38 | 5.37 | 5.37 | 5.36 | 5.34 | 5.35 | 5.36 | 5.39 | 2.85 | 2.69 | 39.957 | 189759 | 52.52 | 40 | 2.5 | 2.78 | 5.26 | 5.14 | 5.29 | 5.16 | 5.2 | 5.32 | 5.31 | 5.28 | 2.78 | 2.66 | 256.2077 | 0.004096
2025-11-27 08:14 | 1179427 | 277 | 250 | 1179428 | 252 | 489 | 978 | 34.5544 | 28.5547 | 4912988 | 280 | 3715161 | 30 | 18400 | 0 | 39.429 | 188716 | 40.81 | 100 | 4.85 | 4.81 | 4.7 | 4.67 | 4.77 | 4.75 | 4.62 | 4.6 | 4.67 | 4.43 | 4.83 | 4.59 | 38.694 | 186972 | 34.65 | 100 | 4.66 | 4.37 | 4.44 | 4.4 | 4.58 | 4.56 | 4.51 | 4.55 | 4.61 | 4.52 | 4.75 | 4.51 | 38.834 | 186534 | 35.19 | 100 | 4.58 | 4.54 | 4.58 | 4.4 | 4.58 | 4.55 | 4.59 | 4.51 | 4.69 | 4.53 | 4.78 | 4.64 | 42.005 | 191944 | 54.06 | 100 | 2.76 | 2.86 | 5.51 | 5.47 | 5.51 | 5.51 | 5.5 | 5.55 | 5.55 | 5.52 | 2.68 | 2.99 | 40.989 | 189967 | 53.2 | 100 | 2.68 | 2.99 | 5.59 | 5.58 | 5.57 | 5.58 | 5.56 | 5.57 | 5.57 | 5.59 | 2.96 | 2.8 | 41.029 | 189760 | 53.16 | 100 | 2.61 | 2.88 | 5.46 | 5.33 | 5.49 | 5.36 | 5.41 | 5.52 | 5.5 | 5.48 | 2.88 | 2.76 | 258.4194 | 1
2025-11-27 08:15 | 1179432 | 281 | 248 | 1179432 | 248 | 480 | 960 | 34.6955 | 28.4889 | 4912994 | 276 | 3715162 | 28 | 18400 | 0 | 38.901 | 188717 | 41.46 | 100 | 4.72 | 4.7 | 4.71 | 4.62 | 4.66 | 4.68 | 4.51 | 4.54 | 4.56 | 4.35 | 4.83 | 4.59 | 38.062 | 186973 | 35.32 | 100 | 4.61 | 4.32 | 4.36 | 4.31 | 4.46 | 4.46 | 4.47 | 4.48 | 4.53 | 4.47 | 4.71 | 4.47 | 38.036 | 186535 | 35.83 | 100 | 4.49 | 4.46 | 4.48 | 4.35 | 4.49 | 4.45 | 4.51 | 4.44 | 4.58 | 4.47 | 4.69 | 4.54 | 40.968 | 191945 | 54.71 | 41 | 2.78 | 2.89 | 5.58 | 5.53 | 5.57 | 5.57 | 5.57 | 5.62 | 5.61 | 5.58 | 2.72 | 3.01 | 41.023 | 189968 | 53.88 | 41 | 2.72 | 3.03 | 5.67 | 5.65 | 5.63 | 5.64 | 5.64 | 5.64 | 5.63 | 5.62 | 3 | 2.82 | 40.964 | 189760 | 53.84 | 41 | 2.63 | 2.9 | 5.52 | 5.38 | 5.54 | 5.41 | 5.47 | 5.57 | 5.55 | 5.53 | 2.91 | 2.79 | 256.4796 | 0.068921
2025-11-27 08:16 | 1179436 | 281 | 237 | 1179436 | 237 | 488 | 976 | 34.8177 | 28.6675 | 4912998 | 260 | 3715162 | 23 | 18400 | 0 | 37.993 | 188717 | 42.08 | 38 | 3.83 | 3.88 | 4.74 | 4.67 | 4.77 | 4.8 | 4.62 | 4.63 | 4.69 | 4.5 | 4.03 | 3.79 | 37.978 | 186974 | 35.89 | 38 | 4.34 | 4.08 | 4.49 | 4.41 | 4.59 | 4.5 | 4.6 | 4.54 | 4.55 | 4.52 | 4.42 | 4.13 | 38.019 | 186535 | 36.5 | 38 | 4.32 | 4.3 | 4.55 | 4.43 | 4.56 | 4.53 | 4.54 | 4.53 | 4.61 | 4.54 | 4.37 | 4.23 | 38.023 | 191945 | 55.37 | 38 | 2.52 | 2.63 | 5.04 | 5.01 | 5.05 | 5.04 | 5.02 | 5.08 | 5.09 | 5.05 | 2.45 | 2.75 | 38.023 | 189969 | 54.55 | 38 | 2.41 | 2.74 | 5.08 | 5.08 | 5.07 | 5.07 | 5.04 | 5.06 | 5.07 | 5.09 | 2.72 | 2.52 | 37.993 | 189761 | 54.51 | 38 | 2.35 | 2.65 | 4.97 | 4.87 | 5.01 | 4.89 | 4.92 | 5.04 | 5.03 | 5 | 2.63 | 2.52 | 245.2092 | 0.0030109
2025-11-27 08:17 | 1179440 | 290 | 246 | 1179440 | 237 | 490 | 980 | 34.9588 | 28.912 | 4913003 | 266 | 3715163 | 20 | 18400 | 0 | 39.793 | 188718 | 42.75 | 38 | 4.88 | 4.86 | 4.76 | 4.7 | 4.81 | 4.84 | 4.66 | 4.61 | 4.72 | 4.56 | 4.94 | 4.7 | 38.781 | 186974 | 36.53 | 39 | 4.67 | 4.39 | 4.55 | 4.46 | 4.55 | 4.58 | 4.56 | 4.57 | 4.54 | 4.57 | 4.81 | 4.55 | 38.727 | 186536 | 37.14 | 39 | 4.65 | 4.62 | 4.57 | 4.44 | 4.59 | 4.55 | 4.55 | 4.48 | 4.67 | 4.59 | 4.79 | 4.65 | 39.984 | 191946 | 56.01 | 39 | 2.68 | 2.8 | 5.38 | 5.35 | 5.39 | 5.38 | 5.36 | 5.42 | 5.42 | 5.39 | 2.62 | 2.92 | 39.374 | 189969 | 55.19 | 39 | 2.54 | 2.89 | 5.36 | 5.35 | 5.35 | 5.34 | 5.32 | 5.34 | 5.35 | 5.37 | 2.85 | 2.66 | 39.003 | 189762 | 55.19 | 39 | 2.43 | 2.74 | 5.15 | 5.03 | 5.18 | 5.05 | 5.1 | 5.21 | 5.2 | 5.17 | 2.73 | 2.6 | 254.6477 | 0.0034285
2025-11-27 08:18 | 1179444 | 294 | 243 | 1179444 | 244 | 489 | 978 | 35.1092 | 28.9403 | 4913007 | 268 | 3715163 | 25 | 18400 | 0 | 39.007 | 188719 | 43.44 | 39 | 4.42 | 4.43 | 4.78 | 4.7 | 4.8 | 4.87 | 4.66 | 4.68 | 4.72 | 4.56 | 4.55 | 4.31 | 38.983 | 186975 | 37.25 | 39 | 4.7 | 4.4 | 4.55 | 4.45 | 4.63 | 4.58 | 4.61 | 4.64 | 4.66 | 4.54 | 4.8 | 4.54 | 38.832 | 186537 | 37.78 | 39 | 4.66 | 4.63 | 4.52 | 4.51 | 4.56 | 4.6 | 4.62 | 4.58 | 4.74 | 4.61 | 4.69 | 4.57 | 38.98 | 191947 | 56.66 | 39 | 2.59 | 2.73 | 5.22 | 5.18 | 5.22 | 5.21 | 5.2 | 5.25 | 5.26 | 5.23 | 2.53 | 2.84 | 38.959 | 189970 | 55.84 | 39 | 2.5 | 2.84 | 5.26 | 5.26 | 5.25 | 5.25 | 5.22 | 5.24 | 5.25 | 5.27 | 2.8 | 2.63 | 38.969 | 189762 | 55.8 | 39 | 2.43 | 2.74 | 5.14 | 5.02 | 5.18 | 5.05 | 5.09 | 5.2 | 5.2 | 5.17 | 2.73 | 2.6 | 251.6759 | 0.0035187
2025-11-27 08:19 | 1179448 | 294 | 247 | 1179448 | 247 | 487 | 974 | 35.2785 | 29.0343 | 4913011 | 274 | 3715163 | 27 | 18400 | 0 | 39.686 | 188719 | 44.06 | 40 | 4.95 | 4.9 | 4.81 | 4.7 | 4.8 | 4.81 | 4.61 | 4.64 | 4.67 | 4.54 | 4.75 | 4.52 | 38.792 | 186976 | 37.86 | 40 | 4.72 | 4.39 | 4.51 | 4.41 | 4.64 | 4.56 | 4.56 | 4.58 | 4.64 | 4.48 | 4.79 | 4.52 | 38.816 | 186537 | 38.43 | 40 | 4.65 | 4.61 | 4.56 | 4.45 | 4.59 | 4.56 | 4.64 | 4.53 | 4.72 | 4.6 | 4.79 | 4.65 | 39.974 | 191947 | 57.36 | 40 | 2.68 | 2.8 | 5.39 | 5.35 | 5.39 | 5.38 | 5.37 | 5.43 | 5.43 | 5.39 | 2.62 | 2.93 | 40.009 | 189971 | 56.46 | 40 | 2.59 | 2.94 | 5.45 | 5.44 | 5.43 | 5.43 | 5.42 | 5.42 | 5.43 | 5.44 | 2.88 | 2.74 | 40.002 | 189763 | 56.46 | 40 | 2.5 | 2.82 | 5.29 | 5.17 | 5.34 | 5.21 | 5.24 | 5.36 | 5.35 | 5.32 | 2.79 | 2.69 | 255.9717 | 0.004096
2025-11-27 08:20 | 1179452 | 302 | 253 | 1179452 | 247 | 486 | 972 | 35.4196 | 29.0907 | 4913016 | 279 | 3715164 | 26 | 18400 | 0 | 39.621 | 188720 | 44.72 | 40 | 4.87 | 4.85 | 4.75 | 4.75 | 4.7 | 4.81 | 4.64 | 4.63 | 4.74 | 4.59 | 4.91 | 4.65 | 38.754 | 186976 | 38.5 | 40 | 4.67 | 4.37 | 4.54 | 4.35 | 4.6 | 4.54 | 4.57 | 4.54 | 4.65 | 4.55 | 4.73 | 4.44 | 38.647 | 186538 | 39.07 | 40 | 4.63 | 4.59 | 4.53 | 4.48 | 4.59 | 4.53 | 4.59 | 4.52 | 4.71 | 4.55 | 4.77 | 4.64 | 39.988 | 191948 | 57.99 | 40 | 2.71 | 2.84 | 5.47 | 5.42 | 5.46 | 5.46 | 5.46 | 5.51 | 5.5 | 5.47 | 2.66 | 2.95 | 39.966 | 189971 | 57.2 | 40 | 2.6 | 2.94 | 5.47 | 5.45 | 5.45 | 5.46 | 5.44 | 5.44 | 5.44 | 5.46 | 2.89 | 2.73 | 40.008 | 189764 | 57.17 | 40 | 2.52 | 2.83 | 5.32 | 5.2 | 5.36 | 5.23 | 5.27 | 5.39 | 5.38 | 5.34 | 2.82 | 2.69 | 262.3205 | 0.004096
2025-11-27 08:21 | 1179456 | 306 | 243 | 1179456 | 243 | 498 | 996 | 35.5418 | 29.1942 | 4913020 | 271 | 3715164 | 28 | 18400 | 0 | 38.956 | 188721 | 45.38 | 39 | 3.96 | 4.02 | 4.83 | 4.84 | 4.85 | 4.88 | 4.8 | 4.74 | 4.87 | 4.68 | 4.17 | 3.93 | 38.961 | 186977 | 39.15 | 39 | 4.48 | 4.19 | 4.58 | 4.52 | 4.71 | 4.65 | 4.69 | 4.71 | 4.67 | 4.69 | 4.58 | 4.28 | 38.995 | 186538 | 39.72 | 39 | 4.46 | 4.45 | 4.66 | 4.57 | 4.7 | 4.59 | 4.73 | 4.65 | 4.81 | 4.69 | 4.64 | 4.48 | 38.97 | 191949 | 58.65 | 39 | 2.58 | 2.71 | 5.19 | 5.16 | 5.2 | 5.19 | 5.17 | 5.23 | 5.24 | 5.2 | 2.52 | 2.83 | 38.989 | 189972 | 57.86 | 39 | 2.48 | 2.84 | 5.25 | 5.24 | 5.24 | 5.24 | 5.21 | 5.23 | 5.24 | 5.25 | 2.77 | 2.64 | 39.014 | 189764 | 57.83 | 39 | 2.41 | 2.74 | 5.12 | 5 | 5.17 | 5.04 | 5.07 | 5.19 | 5.18 | 5.16 | 2.73 | 2.58 | 252.061 | 0.0035187
2025-11-27 08:22 | 1179460 | 306 | 249 | 1179460 | 254 | 505 | 1010 | 35.7299 | 29.3258 | 4913025 | 281 | 3715165 | 32 | 18400 | 0 | 40.355 | 188721 | 46.08 | 100 | 4.18 | 4.23 | 4.98 | 4.84 | 5 | 4.99 | 4.89 | 4.87 | 4.99 | 4.84 | 4.38 | 4.14 | 40.243 | 186978 | 39.85 | 100 | 4.74 | 4.44 | 4.68 | 4.6 | 4.8 | 4.75 | 4.75 | 4.79 | 4.86 | 4.72 | 4.85 | 4.54 | 40.034 | 186539 | 40.38 | 100 | 4.59 | 4.58 | 4.69 | 4.69 | 4.79 | 4.73 | 4.78 | 4.7 | 4.8 | 4.79 | 4.81 | 4.66 | 40.003 | 191949 | 59.31 | 100 | 2.66 | 2.79 | 5.35 | 5.32 | 5.36 | 5.35 | 5.33 | 5.39 | 5.4 | 5.36 | 2.6 | 2.91 | 40.034 | 189973 | 58.49 | 100 | 2.56 | 2.92 | 5.39 | 5.39 | 5.38 | 5.38 | 5.36 | 5.37 | 5.39 | 5.4 | 2.84 | 2.72 | 40.032 | 189765 | 58.49 | 100 | 2.49 | 2.82 | 5.28 | 5.16 | 5.33 | 5.19 | 5.24 | 5.35 | 5.35 | 5.31 | 2.8 | 2.67 | 258.4567 | 1
2025-11-27 08:23 | 1179465 | 314 | 255 | 1179465 | 255 | 507 | 1014 | 35.9086 | 29.26 | 4913030 | 278 | 3715165 | 23 | 18400 | 0 | 41.858 | 188722 | 46.76 | 41 | 5.14 | 5.12 | 5 | 4.96 | 4.99 | 5.03 | 4.92 | 4.89 | 4.94 | 4.93 | 5.1 | 4.88 | 40.723 | 186978 | 40.48 | 41 | 4.83 | 4.59 | 4.71 | 4.64 | 4.82 | 4.77 | 4.79 | 4.82 | 4.87 | 4.77 | 5.01 | 4.72 | 40.414 | 186540 | 41.05 | 41 | 4.85 | 4.79 | 4.77 | 4.68 | 4.82 | 4.74 | 4.84 | 4.71 | 4.88 | 4.81 | 4.99 | 4.84 | 40.984 | 191950 | 60 | 41 | 2.74 | 2.88 | 5.52 | 5.49 | 5.52 | 5.52 | 5.51 | 5.56 | 5.56 | 5.53 | 2.69 | 2.99 | 40.992 | 189973 | 59.21 | 41 | 2.65 | 3.02 | 5.59 | 5.58 | 5.57 | 5.57 | 5.55 | 5.56 | 5.57 | 5.59 | 2.94 | 2.8 | 41.002 | 189766 | 59.18 | 41 | 2.57 | 2.91 | 5.45 | 5.33 | 5.49 | 5.35 | 5.41 | 5.51 | 5.51 | 5.47 | 2.88 | 2.76 | 264.8521 | 0.0047501
2025-11-27 08:24 | 1179469 | 319 | 254 | 1179469 | 258 | 500 | 1000 | 36.0402 | 29.3634 | 4913035 | 284 | 3715166 | 30 | 18400 | 0 | 40.986 | 188723 | 47.44 | 100 | 4.87 | 4.87 | 4.89 | 4.86 | 4.96 | 4.99 | 4.87 | 4.8 | 4.93 | 4.92 | 5.01 | 4.78 | 40.363 | 186979 | 41.19 | 100 | 4.87 | 4.59 | 4.67 | 4.59 | 4.78 | 4.72 | 4.78 | 4.78 | 4.84 | 4.74 | 4.95 | 4.61 | 40.15 | 186541 | 41.72 | 100 | 4.81 | 4.78 | 4.78 | 4.66 | 4.74 | 4.71 | 4.73 | 4.73 | 4.83 | 4.75 | 4.94 | 4.81 | 40.988 | 191951 | 60.69 | 100 | 2.74 | 2.89 | 5.53 | 5.49 | 5.53 | 5.53 | 5.52 | 5.57 | 5.59 | 5.55 | 2.69 | 3.01 | 40.974 | 189974 | 59.86 | 100 | 2.65 | 3.03 | 5.6 | 5.59 | 5.58 | 5.57 | 5.56 | 5.57 | 5.58 | 5.61 | 2.93 | 2.83 | 40.989 | 189766 | 59.86 | 100 | 2.57 | 2.91 | 5.46 | 5.34 | 5.5 | 5.37 | 5.41 | 5.53 | 5.51 | 5.48 | 2.9 | 2.75 | 263.9364 | 1
2025-11-27 08:25 | 1179473 | 319 | 254 | 1179473 | 254 | 497 | 994 | 36.1531 | 29.4669 | 4913039 | 276 | 3715166 | 22 | 18400 | 0 | 41.019 | 188723 | 48.09 | 41 | 4.87 | 4.87 | 5 | 4.84 | 4.84 | 4.88 | 4.78 | 4.78 | 4.91 | 4.91 | 4.97 | 4.76 | 40.198 | 186980 | 41.83 | 41 | 4.85 | 4.56 | 4.7 | 4.57 | 4.78 | 4.7 | 4.73 | 4.8 | 4.82 | 4.72 | 4.97 | 4.7 | 40.093 | 186541 | 42.42 | 41 | 4.76 | 4.73 | 4.75 | 4.64 | 4.78 | 4.71 | 4.79 | 4.69 | 4.87 | 4.71 | 4.96 | 4.81 | 41.038 | 191951 | 61.42 | 41 | 2.75 | 2.9 | 5.55 | 5.51 | 5.55 | 5.54 | 5.53 | 5.58 | 5.58 | 5.55 | 2.69 | 3.01 | 41.007 | 189975 | 60.59 | 41 | 2.67 | 3.03 | 5.63 | 5.62 | 5.61 | 5.61 | 5.6 | 5.6 | 5.6 | 5.63 | 2.95 | 2.84 | 40.987 | 189767 | 60.52 | 41 | 2.57 | 2.9 | 5.46 | 5.33 | 5.5 | 5.36 | 5.41 | 5.52 | 5.51 | 5.48 | 2.89 | 2.75 | 264.0421 | 0.0047501
2025-11-27 08:26 | 1179477 | 327 | 288 | 1179478 | 286 | 499 | 998 | 36.3223 | 29.6832 | 4913044 | 340 | 3715167 | 52 | 18400 | 0 | 41.47 | 188724 | 48.81 | 100 | 5.1 | 5.08 | 5.01 | 4.93 | 4.99 | 5.02 | 4.89 | 4.87 | 4.91 | 4.97 | 5.15 | 4.92 | 40.302 | 186980 | 42.53 | 100 | 4.84 | 4.55 | 4.73 | 4.59 | 4.79 | 4.73 | 4.7 | 4.83 | 4.82 | 4.75 | 4.99 | 4.73 | 40.132 | 186542 | 43.09 | 100 | 4.83 | 4.79 | 4.78 | 4.65 | 4.75 | 4.7 | 4.8 | 4.67 | 4.88 | 4.74 | 4.98 | 4.83 | 51.098 | 191952 | 62.18 | 100 | 5.69 | 5.76 | 6.41 | 6.38 | 6.34 | 6.33 | 6.45 | 6.42 | 6.27 | 6.38 | 5.69 | 5.78 | 51.724 | 189975 | 61.3 | 100 | 6.31 | 6.39 | 6.23 | 6.33 | 6.37 | 6.2 | 6.23 | 6.2 | 6.2 | 6.1 | 6.55 | 6.29 | 51.563 | 189768 | 61.26 | 100 | 6.17 | 6.07 | 6.13 | 5.87 | 6.2 | 5.94 | 6.15 | 6.07 | 6.27 | 6.17 | 6.29 | 5.93 | 299.566 | 1
2025-11-27 08:27 | 1179482 | 331 | 283 | 1179483 | 283 | 489 | 978 | 36.4822 | 29.8806 | 4913050 | 346 | 3715168 | 63 | 18400 | 0 | 40.556 | 188725 | 49.45 | 100 | 4.96 | 4.96 | 4.86 | 4.84 | 4.89 | 4.9 | 4.78 | 4.77 | 4.88 | 4.92 | 5.01 | 4.8 | 39.54 | 186981 | 43.16 | 100 | 4.75 | 4.46 | 4.63 | 4.55 | 4.69 | 4.68 | 4.61 | 4.69 | 4.75 | 4.66 | 4.9 | 4.63 | 39.453 | 186543 | 43.75 | 100 | 4.72 | 4.69 | 4.63 | 4.59 | 4.65 | 4.67 | 4.7 | 4.65 | 4.8 | 4.66 | 4.84 | 4.71 | 51.429 | 191953 | 63.03 | 100 | 6.39 | 6.34 | 6.28 | 6.23 | 6.32 | 6.34 | 6.32 | 6.26 | 6.25 | 6.24 | 6.41 | 6.42 | 50.46 | 189976 | 62.19 | 100 | 6.17 | 6.25 | 6.14 | 6.16 | 6.19 | 6.11 | 6.11 | 6.02 | 6.03 | 5.98 | 6.4 | 6.14 | 50.265 | 189769 | 62.15 | 100 | 5.98 | 5.91 | 5.98 | 5.68 | 6.06 | 5.8 | 6.06 | 5.98 | 6.11 | 6.02 | 6.17 | 5.82 | 294.5322 | 1
2025-11-27 08:28 | 1179487 | 331 | 286 | 1179487 | 286 | 495 | 990 | 36.6703 | 29.8336 | 4913056 | 343 | 3715169 | 57 | 18400 | 0 | 41.043 | 188725 | 50.13 | 100 | 5.03 | 5.01 | 4.96 | 4.83 | 4.94 | 4.98 | 4.83 | 4.82 | 4.85 | 4.98 | 5.06 | 4.86 | 39.948 | 186982 | 43.82 | 100 | 4.75 | 4.51 | 4.65 | 4.62 | 4.79 | 4.72 | 4.73 | 4.76 | 4.79 | 4.72 | 4.97 | 4.71 | 39.906 | 186543 | 44.41 | 100 | 4.84 | 4.78 | 4.74 | 4.65 | 4.78 | 4.7 | 4.81 | 4.68 | 4.86 | 4.7 | 4.9 | 4.78 | 52.002 | 191954 | 63.79 | 100 | 6.36 | 6.39 | 6.2 | 6.3 | 6.41 | 6.39 | 6.36 | 6.22 | 6.24 | 6.28 | 6.47 | 6.5 | 51.071 | 189977 | 63.03 | 100 | 6.2 | 6.29 | 6.24 | 6.23 | 6.28 | 6.12 | 6.19 | 6.13 | 6.16 | 6.06 | 6.49 | 6.22 | 51.027 | 189769 | 63 | 100 | 6.06 | 5.98 | 6.06 | 5.74 | 6.13 | 5.88 | 6.14 | 6.08 | 6.19 | 6.17 | 6.24 | 5.9 | 297.8533 | 1
2025-11-27 08:29 | 1179492 | 341 | 286 | 1179492 | 286 | 495 | 990 | 36.8113 | 29.7866 | 4913062 | 351 | 3715170 | 65 | 18400 | 0 | 41.016 | 188726 | 50.85 | 100 | 4.99 | 4.98 | 4.99 | 4.89 | 4.98 | 4.92 | 4.83 | 4.82 | 4.86 | 4.96 | 5.06 | 4.83 | 40.08 | 186982 | 44.49 | 100 | 4.86 | 4.58 | 4.69 | 4.64 | 4.82 | 4.76 | 4.68 | 4.82 | 4.79 | 4.74 | 4.98 | 4.74 | 40.19 | 186544 | 45.04 | 100 | 4.85 | 4.81 | 4.74 | 4.64 | 4.74 | 4.77 | 4.83 | 4.74 | 4.9 | 4.81 | 4.97 | 4.85 | 51.787 | 191955 | 64.75 | 100 | 6.32 | 6.31 | 6.29 | 6.27 | 6.33 | 6.38 | 6.39 | 6.32 | 6.29 | 6.31 | 6.46 | 6.43 | 50.942 | 189978 | 63.88 | 100 | 6.21 | 6.29 | 6.23 | 6.22 | 6.28 | 6.13 | 6.2 | 6.15 | 6.17 | 6.06 | 6.48 | 6.21 | 51.177 | 189770 | 63.85 | 100 | 6.12 | 6.02 | 6.07 | 5.84 | 6.15 | 5.89 | 6.17 | 6.09 | 6.19 | 6.19 | 6.25 | 5.94 | 298.0025 | 1
2025-11-27 08:30 | 1179497 | 346 | 279 | 1179497 | 279 | 483 | 966 | 36.8866 | 29.8242 | 4913068 | 356 | 3715171 | 77 | 18400 | 0 | 40.189 | 188727 | 51.53 | 100 | 4.95 | 4.93 | 4.8 | 4.74 | 4.88 | 4.87 | 4.75 | 4.72 | 4.8 | 4.83 | 4.94 | 4.72 | 39.107 | 186983 | 45.19 | 100 | 4.7 | 4.42 | 4.58 | 4.5 | 4.69 | 4.63 | 4.61 | 4.64 | 4.69 | 4.56 | 4.85 | 4.58 | 38.958 | 186545 | 45.77 | 100 | 4.71 | 4.67 | 4.64 | 4.54 | 4.67 | 4.64 | 4.67 | 4.59 | 4.76 | 4.64 | 4.83 | 4.69 | 50.541 | 191956 | 65.56 | 100 | 6.13 | 6.15 | 6.15 | 6.13 | 6.24 | 6.18 | 6.23 | 6.14 | 6.09 | 6.13 | 6.31 | 6.32 | 49.464 | 189979 | 64.72 | 100 | 6.05 | 6.13 | 6.06 | 6.04 | 6.1 | 5.92 | 6.03 | 5.96 | 5.97 | 5.87 | 6.34 | 6.04 | 49.409 | 189771 | 64.68 | 100 | 5.89 | 5.81 | 5.87 | 5.57 | 5.94 | 5.69 | 5.96 | 5.88 | 6.01 | 5.97 | 6.06 | 5.73 | 290.7865 | 1
2025-11-27 08:31 | 1179501 | 346 | 287 | 1179502 | 287 | 498 | 996 | 36.9336 | 29.7772 | 4913073 | 361 | 3715172 | 74 | 18400 | 0 | 41.295 | 188727 | 52.16 | 100 | 5.08 | 5.06 | 4.93 | 4.91 | 4.91 | 5 | 4.86 | 4.85 | 4.93 | 5 | 5.09 | 4.86 | 40.28 | 186984 | 45.81 | 100 | 4.9 | 4.6 | 4.74 | 4.65 | 4.84 | 4.71 | 4.71 | 4.84 | 4.81 | 4.74 | 5 | 4.74 | 40.195 | 186545 | 46.39 | 100 | 4.84 | 4.8 | 4.79 | 4.66 | 4.78 | 4.74 | 4.8 | 4.74 | 4.89 | 4.73 | 4.92 | 4.8 | 52.078 | 191956 | 66.46 | 100 | 6.29 | 6.32 | 6.32 | 6.26 | 6.37 | 6.4 | 6.37 | 6.29 | 6.26 | 6.29 | 6.47 | 6.46 | 51.022 | 189980 | 65.55 | 100 | 6.22 | 6.31 | 6.24 | 6.23 | 6.27 | 6.12 | 6.13 | 6.05 | 6.14 | 6.05 | 6.49 | 6.21 | 50.895 | 189772 | 65.52 | 100 | 6.11 | 6 | 6.04 | 5.79 | 6.11 | 5.86 | 6.12 | 6.04 | 6.13 | 6.08 | 6.22 | 5.89 | 299.1745 | 1
2025-11-27 08:32 | 1179506 | 355 | 283 | 1179506 | 283 | 487 | 974 | 36.9524 | 29.8995 | 4913080 | 412 | 3715174 | 129 | 18400 | 0 | 40.61 | 188728 | 52.89 | 100 | 5.03 | 5.02 | 4.85 | 4.83 | 4.88 | 4.92 | 4.78 | 4.78 | 4.85 | 4.85 | 5.01 | 4.79 | 39.695 | 186984 | 46.52 | 100 | 4.81 | 4.52 | 4.65 | 4.58 | 4.71 | 4.72 | 4.68 | 4.8 | 4.74 | 4.73 | 4.91 | 4.65 | 39.819 | 186546 | 47.05 | 100 | 4.8 | 4.76 | 4.74 | 4.64 | 4.69 | 4.7 | 4.75 | 4.71 | 4.88 | 4.73 | 4.91 | 4.79 | 51.065 | 191957 | 67.32 | 100 | 6.2 | 6.22 | 6.21 | 6.12 | 6.3 | 6.24 | 6.18 | 6.2 | 6.15 | 6.19 | 6.32 | 6.32 | 50.178 | 189981 | 66.44 | 100 | 6.15 | 6.21 | 6.11 | 6.13 | 6.15 | 6.08 | 6.04 | 5.99 | 6.03 | 5.96 | 6.37 | 6.11 | 50.335 | 189773 | 66.41 | 100 | 6.03 | 5.92 | 5.96 | 5.63 | 6.04 | 5.79 | 6.06 | 5.99 | 6.14 | 6.09 | 6.15 | 5.84 | 295.0245 | 1
2025-11-27 08:33 | 1179511 | 360 | 283 | 1179511 | 283 | 490 | 980 | 37.0653 | 30.0593 | 4913087 | 401 | 3715176 | 118 | 18400 | 0 | 40.882 | 188729 | 53.53 | 100 | 5.03 | 5.03 | 4.94 | 4.89 | 4.93 | 4.92 | 4.82 | 4.82 | 4.93 | 4.95 | 5.04 | 4.84 | 39.837 | 186985 | 47.18 | 100 | 4.86 | 4.58 | 4.67 | 4.59 | 4.8 | 4.68 | 4.75 | 4.78 | 4.79 | 4.68 | 4.93 | 4.65 | 39.603 | 186546 | 47.71 | 100 | 4.79 | 4.76 | 4.67 | 4.64 | 4.73 | 4.72 | 4.78 | 4.62 | 4.79 | 4.68 | 4.91 | 4.77 | 51.238 | 191958 | 68.17 | 100 | 6.22 | 6.24 | 6.24 | 6.2 | 6.29 | 6.31 | 6.23 | 6.15 | 6.17 | 6.21 | 6.33 | 6.37 | 50.308 | 189981 | 67.22 | 100 | 6.17 | 6.23 | 6.12 | 6.13 | 6.16 | 6.09 | 6.09 | 5.99 | 6.04 | 5.96 | 6.38 | 6.12 | 50.051 | 189774 | 67.19 | 100 | 5.98 | 5.9 | 5.94 | 5.65 | 6.02 | 5.77 | 6.03 | 5.95 | 6.08 | 6.04 | 6.14 | 5.81 | 295.143 | 1
2025-11-27 08:34 | 1179516 | 360 | 286 | 1179516 | 286 | 494 | 988 | 37.2063 | 30.1346 | 4913094 | 397 | 3715178 | 111 | 18400 | 0 | 41.272 | 188729 | 54.25 | 100 | 5.07 | 5.05 | 5.02 | 4.91 | 4.97 | 4.92 | 4.86 | 4.88 | 4.94 | 5.01 | 5.12 | 4.91 | 40.249 | 186986 | 47.84 | 100 | 4.88 | 4.6 | 4.71 | 4.65 | 4.85 | 4.77 | 4.79 | 4.77 | 4.87 | 4.75 | 4.99 | 4.72 | 40.061 | 186547 | 48.34 | 100 | 4.84 | 4.81 | 4.75 | 4.69 | 4.79 | 4.74 | 4.8 | 4.7 | 4.86 | 4.78 | 4.96 | 4.83 | 51.728 | 191959 | 69.02 | 100 | 6.35 | 6.36 | 6.3 | 6.25 | 6.45 | 6.36 | 6.3 | 6.32 | 6.3 | 6.27 | 6.43 | 6.44 | 50.703 | 189982 | 68.15 | 100 | 6.2 | 6.27 | 6.18 | 6.16 | 6.18 | 6.14 | 6.15 | 6.1 | 6.13 | 6.04 | 6.48 | 6.2 | 50.686 | 189774 | 68.03 | 100 | 6.09 | 5.98 | 6.01 | 5.78 | 6.09 | 5.83 | 6.09 | 6.02 | 6.1 | 6.12 | 6.21 | 5.87 | 298.4213 | 1
2025-11-27 08:35 | 1179520 | 370 | 279 | 1179520 | 279 | 483 | 966 | 37.3191 | 30.1628 | 4913099 | 397 | 3715179 | 118 | 18400 | 0 | 40.413 | 188730 | 54.93 | 100 | 4.91 | 4.91 | 4.87 | 4.81 | 4.86 | 4.9 | 4.76 | 4.78 | 4.83 | 4.91 | 4.94 | 4.72 | 39.488 | 186986 | 48.5 | 100 | 4.79 | 4.5 | 4.67 | 4.55 | 4.76 | 4.7 | 4.7 | 4.69 | 4.73 | 4.64 | 4.89 | 4.62 | 39.378 | 186548 | 49.04 | 100 | 4.71 | 4.7 | 4.64 | 4.61 | 4.75 | 4.66 | 4.73 | 4.64 | 4.82 | 4.72 | 4.89 | 4.77 | 50.482 | 191960 | 69.82 | 100 | 6.16 | 6.13 | 6.14 | 6.1 | 6.2 | 6.15 | 6.07 | 6.14 | 6.12 | 6.17 | 6.24 | 6.25 | 49.51 | 189983 | 68.89 | 100 | 6.05 | 6.12 | 6.06 | 6.04 | 6.11 | 5.91 | 6.03 | 5.98 | 5.98 | 5.88 | 6.34 | 6.04 | 49.59 | 189775 | 68.87 | 100 | 5.95 | 5.84 | 5.88 | 5.64 | 5.95 | 5.69 | 5.96 | 5.9 | 5.96 | 5.98 | 6.07 | 5.76 | 291.2342 | 1
2025-11-27 08:36 | 1179525 | 374 | 267 | 1179525 | 267 | 462 | 924 | 37.3756 | 29.843 | 4913107 | 409 | 3715182 | 142 | 18400 | 0 | 38.831 | 188731 | 55.58 | 100 | 4.76 | 4.74 | 4.69 | 4.64 | 4.71 | 4.7 | 4.6 | 4.56 | 4.6 | 4.75 | 4.83 | 4.62 | 37.823 | 186987 | 49.14 | 100 | 4.57 | 4.31 | 4.46 | 4.36 | 4.53 | 4.47 | 4.52 | 4.54 | 4.59 | 4.49 | 4.7 | 4.42 | 37.736 | 186548 | 49.68 | 100 | 4.58 | 4.54 | 4.44 | 4.37 | 4.52 | 4.44 | 4.48 | 4.51 | 4.62 | 4.52 | 4.63 | 4.51 | 47.976 | 191961 | 70.73 | 100 | 5.95 | 5.92 | 5.82 | 5.75 | 5.93 | 5.81 | 5.91 | 5.85 | 5.82 | 5.86 | 5.91 | 5.88 | 47.267 | 189984 | 69.7 | 100 | 5.77 | 5.83 | 5.75 | 5.79 | 5.79 | 5.77 | 5.74 | 5.7 | 5.69 | 5.62 | 6.03 | 5.78 | 47.178 | 189776 | 69.71 | 100 | 5.72 | 5.61 | 5.65 | 5.37 | 5.7 | 5.42 | 5.62 | 5.64 | 5.71 | 5.71 | 5.79 | 5.49 | 278.7641 | 1
2025-11-27 08:37 | 1179529 | 374 | 258 | 1179529 | 257 | 443 | 886 | 37.3662 | 30.1063 | 4913113 | 402 | 3715184 | 144 | 18400 | 0 | 37.431 | 188731 | 56.22 | 100 | 4.65 | 4.63 | 4.55 | 4.47 | 4.57 | 4.53 | 4.43 | 4.4 | 4.47 | 4.54 | 4.66 | 4.46 | 36.538 | 186988 | 49.76 | 100 | 4.47 | 4.19 | 4.31 | 4.18 | 4.37 | 4.33 | 4.37 | 4.38 | 4.43 | 4.34 | 4.53 | 4.27 | 36.461 | 186549 | 50.33 | 100 | 4.43 | 4.38 | 4.33 | 4.19 | 4.39 | 4.33 | 4.4 | 4.3 | 4.44 | 4.35 | 4.47 | 4.34 | 46.324 | 191961 | 71.47 | 100 | 5.68 | 5.7 | 5.61 | 5.57 | 5.74 | 5.61 | 5.71 | 5.66 | 5.63 | 5.63 | 5.68 | 5.69 | 45.48 | 189985 | 70.51 | 100 | 5.59 | 5.64 | 5.52 | 5.58 | 5.56 | 5.54 | 5.51 | 5.41 | 5.46 | 5.39 | 5.78 | 5.55 | 45.459 | 189777 | 70.44 | 100 | 5.47 | 5.38 | 5.45 | 5.07 | 5.46 | 5.27 | 5.47 | 5.41 | 5.54 | 5.5 | 5.57 | 5.29 | 269.3585 | 1
2025-11-27 08:38 | 1179533 | 383 | 240 | 1179534 | 239 | 411 | 822 | 37.3568 | 30.0593 | 4913120 | 388 | 3715187 | 148 | 18400 | 0 | 34.732 | 188732 | 56.79 | 100 | 4.26 | 4.25 | 4.15 | 4.12 | 4.24 | 4.24 | 4.04 | 4.09 | 4.16 | 4.25 | 4.31 | 4.12 | 34.354 | 186988 | 50.35 | 100 | 4.19 | 3.93 | 4.04 | 3.95 | 4.06 | 4.07 | 4.1 | 4.09 | 4.15 | 4.11 | 4.26 | 4.05 | 34.652 | 186550 | 50.89 | 100 | 4.19 | 4.14 | 4.08 | 4.01 | 4.16 | 4.14 | 4.17 | 4.1 | 4.22 | 4.16 | 4.22 | 4.12 | 42.145 | 191962 | 72.21 | 100 | 5.19 | 5.16 | 5.09 | 5.02 | 5.23 | 5.12 | 5.22 | 5.16 | 5.09 | 5.12 | 5.28 | 5.28 | 41.989 | 189985 | 71.24 | 100 | 5.13 | 5.17 | 5.08 | 5.15 | 5.18 | 5.12 | 5.1 | 5.01 | 5.07 | 5.01 | 5.29 | 5.09 | 42.806 | 189778 | 71.22 | 100 | 5.07 | 5 | 5.1 | 4.82 | 5.13 | 4.95 | 5.15 | 5.1 | 5.21 | 5.21 | 5.21 | 4.97 | 250.5577 | 1
2025-11-27 08:39 | 1179537 | 387 | 206 | 1179537 | 205 | 355 | 710 | 37.3474 | 30.1722 | 4913126 | 388 | 3715189 | 182 | 18400 | 0 | 30.097 | 188733 | 57.35 | 100 | 3.74 | 3.69 | 3.64 | 3.56 | 3.64 | 3.68 | 3.57 | 3.53 | 3.62 | 3.63 | 3.72 | 3.53 | 29.787 | 186989 | 50.88 | 100 | 3.65 | 3.39 | 3.44 | 3.42 | 3.52 | 3.52 | 3.55 | 3.58 | 3.59 | 3.56 | 3.7 | 3.5 | 30.136 | 186550 | 51.43 | 100 | 3.65 | 3.6 | 3.55 | 3.5 | 3.61 | 3.58 | 3.64 | 3.61 | 3.72 | 3.64 | 3.68 | 3.58 | 35.896 | 191963 | 72.87 | 100 | 4.43 | 4.4 | 4.34 | 4.27 | 4.41 | 4.32 | 4.39 | 4.36 | 4.36 | 4.37 | 4.5 | 4.45 | 35.732 | 189986 | 71.88 | 100 | 4.39 | 4.41 | 4.3 | 4.38 | 4.4 | 4.34 | 4.29 | 4.28 | 4.26 | 4.24 | 4.51 | 4.35 | 36.63 | 189778 | 71.88 | 100 | 4.4 | 4.31 | 4.35 | 4.16 | 4.37 | 4.23 | 4.39 | 4.35 | 4.48 | 4.45 | 4.46 | 4.27 | 215.0548 | 1
2025-11-27 08:40 | 1179540 | 387 | 183 | 1179540 | 183 | 319 | 638 | 37.2533 | 30.0123 | 4913132 | 381 | 3715192 | 198 | 18400 | 0 | 26.898 | 188733 | 57.82 | 100 | 3.36 | 3.32 | 3.24 | 3.17 | 3.25 | 3.28 | 3.16 | 3.13 | 3.2 | 3.22 | 3.38 | 3.18 | 26.117 | 186989 | 51.34 | 100 | 3.23 | 2.98 | 3.02 | 3.01 | 3.11 | 3.07 | 3.1 | 3.11 | 3.12 | 3.08 | 3.27 | 3.03 | 26.084 | 186551 | 51.92 | 100 | 3.17 | 3.12 | 3.07 | 3.04 | 3.12 | 3.11 | 3.12 | 3.1 | 3.19 | 3.1 | 3.24 | 3.11 | 32.81 | 191963 | 73.39 | 100 | 4.04 | 4.01 | 3.95 | 3.93 | 4.05 | 3.98 | 3.94 | 3.91 | 3.96 | 3.96 | 4.11 | 4.06 | 32.065 | 189987 | 72.4 | 100 | 3.99 | 3.98 | 3.87 | 3.88 | 3.95 | 3.89 | 3.87 | 3.79 | 3.81 | 3.7 | 4.11 | 3.87 | 32.172 | 189779 | 72.41 | 100 | 3.91 | 3.8 | 3.81 | 3.65 | 3.82 | 3.63 | 3.77 | 3.8 | 3.87 | 3.83 | 3.88 | 3.67 | 190.9799 | 1
2025-11-27 08:41 | 1179543 | 394 | 179 | 1179543 | 178 | 313 | 626 | 37.0276 | 29.9465 | 4913139 | 387 | 3715196 | 208 | 18400 | 0 | 26.517 | 188733 | 58.29 | 100 | 3.32 | 3.27 | 3.17 | 3.13 | 3.21 | 3.2 | 3.11 | 3.08 | 3.15 | 3.16 | 3.34 | 3.13 | 25.617 | 186990 | 51.77 | 100 | 3.17 | 2.92 | 2.97 | 2.92 | 3.01 | 3.01 | 3.02 | 3.05 | 3.06 | 2.99 | 3.23 | 3 | 25.541 | 186551 | 52.33 | 100 | 3.1 | 3.05 | 2.97 | 2.93 | 3.02 | 3.01 | 3.04 | 3.03 | 3.09 | 3.02 | 3.19 | 3.04 | 31.99 | 191964 | 73.99 | 100 | 3.95 | 3.92 | 3.87 | 3.79 | 3.94 | 3.85 | 3.89 | 3.85 | 3.8 | 3.82 | 4 | 3.95 | 31.141 | 189987 | 72.96 | 100 | 3.85 | 3.82 | 3.76 | 3.8 | 3.79 | 3.76 | 3.76 | 3.71 | 3.7 | 3.64 | 4.01 | 3.75 | 31.101 | 189779 | 72.97 | 100 | 3.73 | 3.63 | 3.68 | 3.5 | 3.7 | 3.56 | 3.7 | 3.66 | 3.72 | 3.73 | 3.83 | 3.56 | 186.6555 | 1
2025-11-27 08:42 | 1179546 | 397 | 182 | 1179546 | 182 | 316 | 632 | 36.6985 | 29.8806 | 4913144 | 295 | 3715198 | 113 | 18400 | 0 | 26.862 | 188734 | 58.73 | 100 | 3.34 | 3.3 | 3.21 | 3.17 | 3.23 | 3.22 | 3.15 | 3.14 | 3.2 | 3.25 | 3.37 | 3.17 | 26.085 | 186990 | 52.22 | 100 | 3.2 | 2.95 | 2.99 | 2.94 | 3.1 | 3.05 | 3.08 | 3.12 | 3.12 | 3.07 | 3.26 | 3.03 | 25.978 | 186552 | 52.77 | 100 | 3.16 | 3.1 | 3.07 | 2.95 | 3.07 | 3.07 | 3.1 | 3.06 | 3.12 | 3.07 | 3.25 | 3.09 | 32.54 | 191964 | 74.53 | 100 | 4.01 | 3.98 | 3.91 | 3.9 | 3.95 | 3.95 | 3.94 | 3.89 | 3.92 | 3.91 | 4.07 | 4.02 | 31.892 | 189988 | 73.48 | 100 | 3.96 | 3.94 | 3.85 | 3.86 | 3.89 | 3.81 | 3.84 | 3.81 | 3.79 | 3.76 | 4.09 | 3.84 | 31.886 | 189780 | 73.46 | 100 | 3.89 | 3.77 | 3.75 | 3.61 | 3.79 | 3.61 | 3.75 | 3.76 | 3.8 | 3.8 | 3.92 | 3.65 | 189.562 | 1
2025-11-27 08:43 | 1179549 | 397 | 177 | 1179549 | 177 | 306 | 612 | 36.3882 | 29.796 | 4913150 | 299 | 3715201 | 122 | 18400 | 0 | 25.922 | 188734 | 59.17 | 100 | 3.23 | 3.18 | 3.08 | 3.05 | 3.07 | 3.1 | 3.04 | 3 | 3.06 | 3.09 | 3.22 | 3.02 | 25.287 | 186990 | 52.65 | 100 | 3.1 | 2.86 | 2.92 | 2.86 | 3.02 | 2.95 | 2.96 | 3.02 | 3.04 | 2.99 | 3.14 | 2.94 | 25.429 | 186552 | 53.2 | 100 | 3.09 | 3.02 | 2.99 | 2.9 | 3 | 3.02 | 3.04 | 3.02 | 3.04 | 3.02 | 3.13 | 2.99 | 31.247 | 191965 | 75.06 | 100 | 3.8 | 3.77 | 3.75 | 3.73 | 3.83 | 3.77 | 3.78 | 3.71 | 3.74 | 3.76 | 3.9 | 3.87 | 30.963 | 189988 | 73.98 | 100 | 3.82 | 3.79 | 3.73 | 3.74 | 3.76 | 3.7 | 3.72 | 3.69 | 3.66 | 3.65 | 3.84 | 3.64 | 31.239 | 189780 | 73.98 | 100 | 3.78 | 3.66 | 3.62 | 3.53 | 3.71 | 3.56 | 3.68 | 3.69 | 3.73 | 3.74 | 3.78 | 3.56 | 184.1513 | 1
2025-11-27 08:44 | 1179552 | 403 | 165 | 1179552 | 165 | 288 | 576 | 36.0402 | 29.4575 | 4913155 | 308 | 3715203 | 143 | 18400 | 0 | 24.305 | 188735 | 59.59 | 100 | 3.02 | 2.97 | 2.89 | 2.82 | 2.85 | 2.92 | 2.82 | 2.81 | 2.88 | 2.89 | 3.04 | 2.83 | 23.73 | 186991 | 53.06 | 100 | 2.92 | 2.69 | 2.75 | 2.73 | 2.82 | 2.78 | 2.79 | 2.84 | 2.84 | 2.77 | 2.96 | 2.74 | 24.052 | 186552 | 53.59 | 100 | 2.84 | 2.79 | 2.79 | 2.76 | 2.82 | 2.84 | 2.86 | 2.83 | 2.91 | 2.86 | 2.96 | 2.83 | 29.153 | 191966 | 75.53 | 100 | 3.59 | 3.55 | 3.5 | 3.45 | 3.55 | 3.51 | 3.54 | 3.46 | 3.49 | 3.49 | 3.61 | 3.56 | 28.757 | 189989 | 74.5 | 100 | 3.54 | 3.53 | 3.45 | 3.44 | 3.49 | 3.44 | 3.47 | 3.43 | 3.42 | 3.39 | 3.63 | 3.42 | 29.132 | 189781 | 74.51 | 100 | 3.51 | 3.4 | 3.36 | 3.27 | 3.43 | 3.3 | 3.43 | 3.43 | 3.49 | 3.46 | 3.48 | 3.29 | 171.4548 | 1
2025-11-27 08:45 | 1179555 | 406 | 173 | 1179555 | 174 | 303 | 606 | 35.6641 | 29.4481 | 4913160 | 307 | 3715205 | 134 | 18400 | 0 | 25.948 | 188735 | 60 | 100 | 3.24 | 3.18 | 3.09 | 3.06 | 3.08 | 3.1 | 3.02 | 2.96 | 3 | 3.07 | 3.27 | 3.05 | 24.695 | 186991 | 53.46 | 100 | 3.05 | 2.8 | 2.85 | 2.81 | 2.9 | 2.86 | 2.87 | 2.86 | 2.86 | 2.85 | 3.09 | 2.8 | 24.18 | 186553 | 54.01 | 100 | 2.94 | 2.88 | 2.84 | 2.78 | 2.85 | 2.86 | 2.87 | 2.84 | 2.87 | 2.84 | 3.02 | 2.85 | 31.482 | 191966 | 76.03 | 100 | 3.93 | 3.87 | 3.77 | 3.75 | 3.82 | 3.8 | 3.74 | 3.74 | 3.72 | 3.67 | 3.92 | 3.84 | 30.165 | 189989 | 74.96 | 100 | 3.8 | 3.77 | 3.68 | 3.67 | 3.68 | 3.61 | 3.64 | 3.59 | 3.57 | 3.53 | 3.84 | 3.56 | 29.613 | 189781 | 74.97 | 100 | 3.64 | 3.52 | 3.51 | 3.37 | 3.52 | 3.39 | 3.52 | 3.49 | 3.51 | 3.48 | 3.7 | 3.39 | 179.5285 | 1
2025-11-27 08:46 | 1179558 | 406 | 201 | 1179558 | 202 | 347 | 694 | 35.2973 | 29.2788 | 4913165 | 295 | 3715207 | 94 | 18400 | 0 | 29.553 | 188736 | 60.46 | 100 | 3.68 | 3.63 | 3.49 | 3.47 | 3.54 | 3.52 | 3.43 | 3.37 | 3.49 | 3.52 | 3.72 | 3.5 | 28.571 | 186992 | 53.9 | 100 | 3.49 | 3.22 | 3.32 | 3.25 | 3.38 | 3.3 | 3.35 | 3.37 | 3.33 | 3.34 | 3.56 | 3.29 | 28.131 | 186553 | 54.44 | 100 | 3.4 | 3.34 | 3.3 | 3.24 | 3.32 | 3.29 | 3.29 | 3.3 | 3.37 | 3.27 | 3.48 | 3.31 | 36.75 | 191967 | 76.63 | 100 | 4.51 | 4.47 | 4.36 | 4.37 | 4.45 | 4.39 | 4.4 | 4.35 | 4.29 | 4.36 | 4.5 | 4.44 | 35.353 | 189990 | 75.53 | 100 | 4.34 | 4.34 | 4.27 | 4.26 | 4.28 | 4.15 | 4.15 | 4.15 | 4.09 | 4.11 | 4.46 | 4.19 | 34.979 | 189782 | 75.53 | 100 | 4.21 | 4.09 | 4.1 | 3.92 | 4.09 | 3.95 | 4.11 | 4.08 | 4.12 | 4.12 | 4.26 | 3.96 | 208.3147 | 1
2025-11-27 08:47 | 1179562 | 412 | 219 | 1179562 | 219 | 374 | 748 | 35.0716 | 29.354 | 4913170 | 304 | 3715208 | 85 | 18400 | 0 | 32.173 | 188736 | 60.95 | 100 | 3.94 | 3.9 | 3.83 | 3.78 | 3.82 | 3.82 | 3.73 | 3.71 | 3.8 | 3.86 | 4.02 | 3.79 | 30.84 | 186992 | 54.4 | 100 | 3.75 | 3.48 | 3.55 | 3.5 | 3.61 | 3.6 | 3.58 | 3.61 | 3.65 | 3.59 | 3.83 | 3.55 | 30.518 | 186554 | 54.93 | 100 | 3.68 | 3.62 | 3.59 | 3.52 | 3.59 | 3.56 | 3.56 | 3.54 | 3.67 | 3.58 | 3.79 | 3.61 | 39.718 | 191967 | 77.27 | 100 | 4.88 | 4.84 | 4.72 | 4.7 | 4.8 | 4.79 | 4.76 | 4.71 | 4.63 | 4.72 | 4.86 | 4.82 | 38.467 | 189990 | 76.18 | 100 | 4.73 | 4.73 | 4.59 | 4.63 | 4.67 | 4.58 | 4.57 | 4.53 | 4.51 | 4.47 | 4.82 | 4.54 | 38.239 | 189783 | 76.18 | 100 | 4.61 | 4.47 | 4.47 | 4.29 | 4.47 | 4.32 | 4.48 | 4.46 | 4.53 | 4.48 | 4.62 | 4.32 | 226.7889 | 1
2025-11-27 08:48 | 1179565 | 416 | 242 | 1179566 | 242 | 413 | 826 | 34.9682 | 29.4669 | 4913175 | 321 | 3715210 | 79 | 18400 | 0 | 35.497 | 188737 | 61.54 | 100 | 4.36 | 4.31 | 4.24 | 4.18 | 4.25 | 4.2 | 4.11 | 4.06 | 4.19 | 4.22 | 4.38 | 4.15 | 34.141 | 186993 | 54.94 | 100 | 4.15 | 3.87 | 3.95 | 3.91 | 4.04 | 3.99 | 3.99 | 3.99 | 4.03 | 3.95 | 4.22 | 3.9 | 33.703 | 186554 | 55.47 | 100 | 4.06 | 4 | 3.96 | 3.88 | 3.97 | 3.95 | 3.96 | 3.96 | 4.05 | 3.94 | 4.16 | 3.98 | 43.877 | 191968 | 77.96 | 100 | 5.39 | 5.36 | 5.19 | 5.21 | 5.35 | 5.3 | 5.17 | 5.23 | 5.14 | 5.24 | 5.38 | 5.35 | 42.16 | 189991 | 76.82 | 100 | 5.13 | 5.13 | 4.97 | 5.09 | 5.11 | 5.03 | 5.01 | 4.89 | 4.93 | 4.86 | 5.32 | 5.02 | 42.156 | 189783 | 76.81 | 100 | 5.06 | 4.93 | 4.9 | 4.75 | 4.95 | 4.78 | 4.96 | 4.91 | 5 | 4.91 | 5.06 | 4.74 | 250.5154 | 1
2025-11-27 08:49 | 1179570 | 416 | 252 | 1179570 | 253 | 431 | 862 | 34.9682 | 29.4481 | 4913181 | 317 | 3715211 | 65 | 18400 | 0 | 36.956 | 188737 | 62.15 | 100 | 4.52 | 4.49 | 4.41 | 4.37 | 4.39 | 4.42 | 4.3 | 4.28 | 4.36 | 4.39 | 4.54 | 4.32 | 35.963 | 186993 | 55.52 | 100 | 4.34 | 4.06 | 4.17 | 4.11 | 4.27 | 4.21 | 4.26 | 4.26 | 4.28 | 4.24 | 4.41 | 4.12 | 35.799 | 186555 | 56.02 | 100 | 4.3 | 4.26 | 4.22 | 4.12 | 4.2 | 4.21 | 4.2 | 4.21 | 4.32 | 4.22 | 4.4 | 4.25 | 45.256 | 191969 | 78.67 | 100 | 5.54 | 5.51 | 5.34 | 5.37 | 5.52 | 5.49 | 5.47 | 5.4 | 5.34 | 5.44 | 5.55 | 5.52 | 44.249 | 189992 | 77.54 | 100 | 5.35 | 5.38 | 5.21 | 5.35 | 5.38 | 5.28 | 5.22 | 5.18 | 5.17 | 5.17 | 5.55 | 5.29 | 44.268 | 189784 | 77.54 | 100 | 5.3 | 5.18 | 5.23 | 4.97 | 5.21 | 5.04 | 5.23 | 5.07 | 5.29 | 5.24 | 5.36 | 5.07 | 260.8673 | 1
2025-11-27 08:50 | 1179574 | 424 | 253 | 1179574 | 254 | 434 | 868 | 35.0246 | 29.5139 | 4913186 | 328 | 3715212 | 75 | 18400 | 0 | 37.103 | 188738 | 62.73 | 100 | 4.56 | 4.54 | 4.44 | 4.39 | 4.47 | 4.46 | 4.33 | 4.32 | 4.38 | 4.46 | 4.6 | 4.38 | 36.043 | 186994 | 56.09 | 100 | 4.36 | 4.08 | 4.17 | 4.1 | 4.23 | 4.24 | 4.25 | 4.23 | 4.29 | 4.19 | 4.44 | 4.16 | 35.93 | 186555 | 56.62 | 100 | 4.31 | 4.26 | 4.17 | 4.11 | 4.25 | 4.17 | 4.24 | 4.16 | 4.31 | 4.18 | 4.41 | 4.25 | 45.544 | 191969 | 79.47 | 100 | 5.64 | 5.59 | 5.43 | 5.43 | 5.53 | 5.47 | 5.5 | 5.46 | 5.41 | 5.43 | 5.52 | 5.49 | 44.337 | 189992 | 78.28 | 100 | 5.43 | 5.45 | 5.36 | 5.37 | 5.39 | 5.23 | 5.23 | 5.22 | 5.19 | 5.12 | 5.57 | 5.3 | 44.276 | 189785 | 78.27 | 100 | 5.28 | 5.18 | 5.2 | 4.99 | 5.24 | 5.05 | 5.25 | 5.2 | 5.29 | 5.26 | 5.33 | 5.03 | 261.9546 | 1
2025-11-27 08:51 | 1179578 | 428 | 270 | 1179578 | 271 | 462 | 924 | 35.1374 | 29.6079 | 4913191 | 365 | 3715213 | 95 | 18400 | 0 | 39.564 | 188739 | 63.4 | 100 | 4.78 | 4.76 | 4.77 | 4.66 | 4.76 | 4.79 | 4.61 | 4.55 | 4.71 | 4.71 | 4.86 | 4.64 | 38.502 | 186995 | 56.75 | 100 | 4.65 | 4.35 | 4.5 | 4.42 | 4.57 | 4.51 | 4.56 | 4.6 | 4.57 | 4.52 | 4.7 | 4.38 | 38.017 | 186556 | 57.23 | 100 | 4.55 | 4.51 | 4.5 | 4.41 | 4.56 | 4.53 | 4.57 | 4.45 | 4.58 | 4.48 | 4.68 | 4.53 | 48.602 | 191970 | 80.25 | 100 | 6 | 5.95 | 5.85 | 5.79 | 5.9 | 5.84 | 5.89 | 5.85 | 5.8 | 5.81 | 5.87 | 5.85 | 47.347 | 189993 | 79.04 | 100 | 5.8 | 5.84 | 5.68 | 5.74 | 5.79 | 5.68 | 5.66 | 5.61 | 5.61 | 5.56 | 5.91 | 5.64 | 47.202 | 189785 | 79.03 | 100 | 5.67 | 5.54 | 5.57 | 5.33 | 5.61 | 5.38 | 5.57 | 5.49 | 5.67 | 5.61 | 5.69 | 5.38 | 279.6677 | 1
2025-11-27 08:52 | 1179583 | 428 | 278 | 1179583 | 279 | 476 | 952 | 35.2785 | 29.6644 | 4913198 | 340 | 3715215 | 62 | 18400 | 0 | 40.982 | 188739 | 64.03 | 100 | 5.06 | 5.03 | 4.9 | 4.87 | 4.97 | 4.92 | 4.81 | 4.76 | 4.83 | 4.91 | 5.08 | 4.85 | 39.615 | 186995 | 57.39 | 100 | 4.82 | 4.53 | 4.65 | 4.53 | 4.65 | 4.67 | 4.67 | 4.7 | 4.72 | 4.61 | 4.88 | 4.57 | 39.204 | 186557 | 57.91 | 100 | 4.71 | 4.67 | 4.58 | 4.52 | 4.69 | 4.63 | 4.7 | 4.64 | 4.74 | 4.56 | 4.82 | 4.67 | 50.23 | 191971 | 81.07 | 100 | 6.21 | 6.17 | 6.06 | 5.99 | 6.1 | 6.03 | 6.08 | 6.08 | 5.98 | 5.99 | 6.2 | 6.17 | 48.865 | 189994 | 79.88 | 100 | 5.97 | 6.02 | 5.92 | 5.92 | 5.96 | 5.8 | 5.82 | 5.8 | 5.83 | 5.66 | 6.19 | 5.88 | 48.632 | 189786 | 79.82 | 100 | 5.81 | 5.68 | 5.73 | 5.5 | 5.78 | 5.57 | 5.79 | 5.71 | 5.82 | 5.78 | 5.84 | 5.53 | 288.0977 | 1
2025-11-27 08:53 | 1179587 | 437 | 290 | 1179588 | 290 | 496 | 992 | 35.4384 | 29.9465 | 4913203 | 366 | 3715216 | 76 | 18400 | 0 | 42.427 | 188740 | 64.8 | 100 | 5.16 | 5.15 | 5.07 | 4.96 | 5.11 | 5.17 | 5 | 4.94 | 5.02 | 5.11 | 5.27 | 5.04 | 41.379 | 186996 | 58.03 | 100 | 5.02 | 4.71 | 4.83 | 4.73 | 4.92 | 4.89 | 4.89 | 4.96 | 4.89 | 4.77 | 5.08 | 4.77 | 41.084 | 186557 | 58.57 | 100 | 4.88 | 4.89 | 4.88 | 4.76 | 4.91 | 4.82 | 4.89 | 4.87 | 4.94 | 4.81 | 5.09 | 4.91 | 51.985 | 191972 | 81.92 | 100 | 6.4 | 6.37 | 6.26 | 6.24 | 6.35 | 6.27 | 6.28 | 6.29 | 6.25 | 6.25 | 6.39 | 6.4 | 50.881 | 189995 | 80.71 | 100 | 6.21 | 6.26 | 6.15 | 6.19 | 6.18 | 6 | 6.12 | 6.07 | 6.07 | 5.86 | 6.41 | 6.13 | 50.726 | 189787 | 80.69 | 100 | 6.04 | 5.91 | 5.96 | 5.72 | 6.03 | 5.82 | 6.04 | 5.96 | 6.08 | 6.03 | 6.16 | 5.81 | 300.7035 | 1
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[114 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0

## Evaluation Warning
This document was generated using a trial version of DevExpress libraries and can only be used for evaluation purposes.
Please purchase a license to continue use of DevExpress product libraries (v25.1.3.0)

## Evaluation Warning (1)
This document was generated using a trial version of DevExpress libraries and can only be used for evaluation purposes.
Please purchase a license to continue use of DevExpress product libraries (v25.1.3.0)